## Slide 1: RT (*) cables terminations and routing to current leads according to baseline
D. De Luca, J-Cl. Guillaume
(*) RT = Room Temperature
Notes: This presentation was already done in HL-MCF meeting February 2017
Is referenced to the BASELINE

## Slide 2: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 3: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 4: Electrical Circuit…as per Baseline
mechanic (tunnel)
UR Point 1, 5
UR Point 1, 5
RR Point 7
RR Point 1, 5
RR Point 1, 5
Warm cabling is located between current leads and power converters
Notes: We focus the attention to the Converter in UR and specially for WCC 13kA ,18kA 2kA

## Slide 5: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 6: Main Requirements…baseline
according to converter and DFH layout
Notes: In RED Details of electrical circuit of the converter shown in previous drawings

## Slide 7: Cable Type Selection
Based on the requirements shown before
Taken into account the rated current of cables (Icable)
  Constraints: decrease power losses to minimise heat dissipation
  If Icable ≤ 600 A  Standard air cooled cable (ACC)
  If Icable > 600 A  Water cooled cable (WCC)
Intensity | Type
120 A | ACC
200 A | ACC
600 A | ACC
2 kA | WCC
13 kA | WCC
18 kA | WCC
Notes: Selection proposed according and to follow constraint of the dynamic of the circuit

## Slide 8: Cable Section Selection
ACC section selection: norm NF C 15-100 assuming
  three cable layers (0.73 of Icable r*)
  > 9 cables touching on cable ladders (0.78 of Icable r*)
  Resulting factor of 0.57 of Icable r*
WCC section selection: technological constraints  LHC and other experiences at CERN
  500 mm2 rated at 3.5 kA  7 A/mm2
  1300 mm2 rated at 8 kA  6.2 A/mm2
  2000 mm2 rated at 13 kA  6.5 A/mm2
* Icable r: rated current of a single cable without taking into account installation reduction factors
Notes: Section have been chosen in accordance of NF C15-100 and for WCC selection based on experience on LHC and Test Areas SM18

## Slide 9: Cable Proposal by EN-EL…baseline
Remarks
  Standard ACC are well known at CERN
  Further studies focused on WCC
Intensity | Section [mm2] | Type
120 A | 70 | ACC
200 A | 95 | ACC
600 A | 400 | ACC
2 kA | 500 | WCC
13 kA | 2000 | WCC
18 kA | 2x1300 | WCC
Notes: Max length of WCC:
Hose: 40m max
Cable assembly: suppliers are not equipped to assemble cables >40m.
Just 3 European suppliers available that are able to meet CERN standards
ACC: Insulation test at 4xUo DC  4x600V=2400V DC during 1min

## Slide 10: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 11: Introduction to WCC’s
water in/out
hose crimping zone
screw fixations
cable crimping zone
water in/out flow mainly
through outside-holes
between lug and hose
cable placed inside lug
Example: WCC lug, 500 mm2 – FLOHE company
Notes: Typical WCC lug 500mm2 where can be identified the hose Crimping zone and cable crimping zone
The cable is crimped inside the lug
The hose is crimped outside the lug

## Slide 12: WCC Technologies
Cable bundle braised on the lug: WCC with spring (BRAR, 2000mm2)
Cable bundle crimped on the lug: WCC without spring (FLOHE, 2000mm2)
Notes: Two different technologies and suppliers (FLOHE – BRAR) are shown
Cable bundle crimped on lugs and Copper Braid braised on the lug
The SPRING used by BRAR have an effect to increase the cable rigidity.

## Slide 13: Main WCC Suppliers in Europe
FLOHE | BRAR | GECSA
Standard Sections [mm2] | Standard Sections [mm2] | Standard Sections [mm2]
500 | 900 | 2500
800 | 1200 | No cables below 2500 mm2
1000 | 1500 | 
1300 | 1800 | 
2000 | 2100 | 
WCC with cable bundle crimped on lug
WCC with cable bundle braised on lug
Three main suppliers in Europe
Relevant information taken from suppliers catalogues
  Suppliers usually provide cables with non-standard sections

## Slide 14: LHC WCC Specifications
Cross-section [mm2] | Nominal current [kA] | Leakage current [µA/m] | DC voltage test level [kV]
500 | 3.5 | 10 @ 3.0 kV | 3
800 | 6.0 | 20 @ 1.5 kV | 3
1000 | 8.0 | 20 @ 1.5 kV | 3
1300 | 8.0 | 30 @ 1.5 kV | 3
2000 | 13.0 | 40 @ 3.0 kV | 3
Normal usage | 
Voltage level | 500 V DC
Highest transitory voltage | 500 V
Operating temperature (hose) | 50 °C
Cooling water pressure in operation | 16 bar
Rated pressure | 24 bar
Water pressure drop | < 2 bar
Water speed | < 2.5 m/s
Maximum input water temperature | 28 °C
Maximum delta T (water in/out) | 15 K

## Slide 15: LHC WCC Installation Example: DFBAK.5L6
6 kA
1000 mm2
13 kA
2000 mm2
Notes: We can observe Current Leads and Cable lugs
Special support and suspension are needed to avoid stress on Current Leads
Space on top of Current leads shall be reserved

## Slide 16: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 17: Dimensional Constraints
DFH
400 mm
200 A & 120 A
2 kA
1000 mm
1200 mm
1300 mm
h
r
6 kA
13 kA & 18 kA
Space reserved
for access.
1000 mm
600 mm
600 A
Cable trays
Area reserved
for cable supports
Cables for circuits:
Intensity | Section [mm2] | h [mm] | r [mm] | Ext. Diam. [mm]
18 kA | 2x1300 | 500 | 800 | 2x95
13 kA | 2000 | 500 | 800 | 115
6 kA | 1000 | 500 | 700 | 95
2 kA | 500 | 500 | 500 | 70
600 A | 400 | 300 | 300 | 36
200 A | 95 | 200 | 200 | 25
120 A | 70 | 150 | 150 | 22
most significant constraints
Notes: The MAIN design constraint is the BENDING RADIUS of the WCC that must be respected
Space shall be reserved on top DFH for cable support / suspension. Can be utilized also during operation and maintenance to access the current lead

## Slide 18: Accessibility
Accessibility to WCC support (installation & maintenance)
Space needed for installation
  Large bending radius
  Manipulation of the cable
  Demineralised water infrastructure
Cable installation to be done before placing DFH’s
Mockup DFB (LHC installation)
Mockup power converters (LHC installation)
Notes: As experience in LHC a mockup has been installed for Current lead and power converters

## Slide 19: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 20: Power Converter and DFHX Layout (1/2)
special support for WCC
adjustable individual supports for WCC
Proposed layout with max 2 cables per current lead
Layout only for WCC
18 kA
13 kA
2 kA
2 kA
Notes: Layout Integration study
Position of converter for optimization of cable length for minimize the length and the heat losses
The sequence of current lead shall be deduct from the cable layout and defined to minimize the WCC length

## Slide 21: Power Converter and DFHX Layout (2/2)
Cable tray positioning constraints:
Depending on converter/DFH alignment
Maintain current leads accessible and removable (LHC)
Cables shall not exert mechanical stress on the current leads when connected
 cable trays are not aligned in order to fulfill the constraints
Front view
Top view
Side view
Notes: Converter layout has impact on the DC WWC layout to minimize the length and avoid overlapping of cables in proximity of Current Leads

## Slide 22: DFH Interface for 3 Cables
3 cables per current lead at DFHX
  2x1300 mm2
  1x500 mm2
HL-LHC: Solution 2
HL-LHC: Solution 1
Applied solution for LHC TOTEM 2 cables per current lead
DFHX – 3 cables per current lead
Not to be used as discussed with Jerome Feiter

## Slide 23: Current Lead Interface for WCC Cables
13kA
  WCC 1x2000 mm2
18kA
  WCC 2x1300 mm2
Current Lead dimensions (WxH)
83 x 242 mm
SLead = 20086 mm2
Current density 0.89 A/mm2
Constraint: Same Interface with Current Lead
Proposed solutions to be confirmed after integration study

## Slide 24: Current Lead Interface for WCC Cables
2kA
  WCC 500 mm2
Current Lead dimensions (WxH)
40 x 76 mm
SLead = 3040 mm2
Current density
0.76 A/mm2
Contact Surface
40 x 66 mm
Scontact = 2640 mm2
Proposed solutions to be confirmed after integration study

## Slide 25: Current Lead Interface for WCC Cables
18kA + 2kA (TRIM)
  WCC 2x1300 mm2 +1x500 mm2
Current Lead dimensions (WxH)
83 x 242 mm
SLead = 20086 mm2
Proposed solutions to be confirmed after integration study
WCC not on the same plane
Current density 0.89 A/mm2

## Slide 26: Current Leads / Converters Arrival of cables on equipment
I – Vertical on Current Leads
II – Vertical on Converter Bus Bar
Requires Suspension / Supports to avoid stress on current lead
Dedicated Cable tray
Support (avoid damage of the hose)

## Slide 27: Current Leads / Converters Interface for WCC Cables
III – Horizontal on Converter busbar
IV - Inclined on current Leads
- Less stress on bus bar
- Cable need space on Converter side
- No Suspension / Support from top
- Plates between Converter and cables
Reduce stress on current leads
Suspension / Support
Reduce space between Current lead and vault
Possible Angle 30º

## Slide 28: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 29: LHC DC-Scheme Example: Point 5 Left
HL-LHC DC scheme ongoing
RQ5.L5B1
RQ5.L5B2
Notes: Drawing requested by HL-MCF and realized by EN-EL -DDO

## Slide 30: LHC Equipment Layout Example: RR53
RQ5.L5B2
RQ5.L5B1
Notes: Equipment Layout realized and maintained by EN-EL

## Slide 31: Existing Relation between Databases: Example of 2 Cables Installed at LHC RQ5.L5
DFBLD.A7L5
Elements (circuit names) make link between databases
Database for installations – Cablothèque
Technical database – Layout Database
DC-Scheme
Notes: Circuit name makes link between databases
Elements are links between database EN-EL and electrical DC scheme
Additional field in GESMAR recently for DC Circuit Name

## Slide 32: Table of Contents
Electrical Circuit
Cable Requirements
Water Cooled Cables Specifications
Installation Constraints
Water Cooled Cable Layout
Documentation
Open Issues

## Slide 33: Open Issues
Sections Optimised?
  Cables adapted to electrical circuit parameters ?
  Current profile ?
  Other constraints ?
Position and size of DFH’s?
  For further studies on cabling  details on DFH’s and power converters necessary (exact position, connection technology)
Separator (Disconnector) ?

## Slide 34: First Attempt of Separator Location (1/2)
real-size separator
support example of separator
HL-LHC UR-section
DFHX

## Slide 35: First Attempt of Separator Location (2/2)
3 cables
1) separators on top of DFH
real-size separator
Possible to locate separators on top of current leads?
2)
2)
3)

## Slide 36: Open Questions (?)
1) Decision about circuit separators
  Are they needed?
  What model, which size (technical specifications)
  Adaptation to cable connection constraints: Interfaces/adaptation of standard model?
  For commissioning of DC-circuits – short-circuit test: How to integrate separator in the test?
2) How to connect WCC’s to separator?
  Allowable weight of cables on separator?
  Space for WCC & water flexibles sufficient?
  Accessibility to WCC guaranteed during and after installation?
3) How to support/fix separator?
  Possible conflict with WCC accessibility?

## Slide 37: Thank you for your attention!

## Slide 38
Additional Slides

## Slide 39: Cable Bending Radius Dependence
External diameter
Hose thickness
Hose material and constitution
Applied water pressure
Cable section
Wire section
Way of winding wires to a bunch
Winding step (distance per turn of wire/bunch)
Technology: spring/no spring