## Slide 1: Cooling of particle detectors
Bart Verlaat, 15 February 2017

## Slide 2: Why is cooling needed in particle detectors?
Electronics produce heat
  When the heat is not removed, the temperature will increase
  Too warm electronics will be damaged
  A detector is full of electronics
  Some of them need to be cold <-10°C
Total heat load of CMS:
  Inside the detector:
    Warm (10°C- 40°C): 700 kilowatt (2000 game PC’s)
    Cold: (<- 10°C): 140 kilowatt (400 game PC’s)
  Outside the detector:
    Warm (10°C- 40°C): 2.600 kilowatt (7.600 game PC’s)
Cooling systems need to cool and reject the heat of about 10.000 game PC’s (325 Watt each)
140 kW
700 kW
2600 kW

## Slide 3: Processor cooling
The limit of processor speed is by the temperature,
faster processors need better cooling.
Same problem with detectors, but we don’t want the usual processor cooling in our detector.
We need something much smaller and much lighter.

## Slide 4: Silicon detector cooling
The silicon tracker need to be cold <-10’C, otherwise the silicon will get damaged due to radiation.
Silicon get damaged
Silicon produces
more heat
Silicon is not cold enough
Silicon gets warmer
Silicon layers

## Slide 5: Detector cooling
Detectors generate a substantial amount of waste heat, just putting it in a cold environment is not enough.
Heat must be removed at the heat source and transferred to the cooling machine.
  Like the advanced processor cooling systems
Just like a processor, the heat must be cooled close to the silicon detector
Heat

## Slide 6: Boiling water
Boiling at 100’C
Dry-out, potatoes are burning at high temperature
Fast boiling (115’C) under pressure
A
C
B
Slow cooking (90’C) in the mountains

## Slide 7: Liquid and evaporative cooling
Flow
Flow
Temperature
Temperature
Fluid
Tube wall
Fluid
Tube wall
Bubbles
Best performance
Cross section of an ATLAS stave

## Slide 8: So the boiling temperature depends on the pressure
We can make 20’C water boil and freeze, just by lowering the pressure
Water (H2O)
But we cannot go lower than 0’C, we need another fluid which can do this => Carbondioxide (CO2)
Detector cooling range

## Slide 9: The Pressure-Enthalpy diagram
100
0
100
200
300
400
500
600
10
5.2
1
20’C
-40’C
Enthalpy (Energy) (kJ/kg)
Pressure (Bar)
Density line
400 (g/l)
A 10 liter bottle with 4kg CO2
-78’C

## Slide 10: How does a CO2 fire extinguisher works?
100
0
100
200
300
400
500
10
5.2
1
20’C
-40’C
Enthalpy (Energy) (kJ/kg)
Pressure (Bar)
400 (g/l)
-78’C
Expanding liquid to atmosphere (1 bar) from a 20’C bottle makes CO2 ice and gas. The ice cools the fire, the gas shields the fire from oxygen.

## Slide 11: How to cool a detector with CO2?
100
0
100
200
300
400
500
10
5.2
1
20’C
-40’C
Enthalpy (Energy) (kJ/kg)
Pressure (Bar)
400 (g/l)
-78’C
If we expand to 10 bar we have a liquid-gas mixture of -40’C, and can cool electronics
Expansion without heat exchange
Heat exchange without pressure change
In reality we do not vent to atmosphere but reuse the gas by pumping it back into the bottle

## Slide 12: CO2 cooling systems for HEP detectors
2008
2009
2010
2011
2012
2013
2PACL concept
AMS 2
LHCb Velo
CORA/SR1 (+Nikhef, Lyon, Aachen, DESY…): ~2 kW @ -20 ˚C
MARCO: 1 kW @ -40 ˚C
CMS Pix-Ph1 “TIF proto”: 15 kW @ -25 ˚C
ATLAS IBL: 2 x 3 kW @ -35 ˚C
CMS Pix-Ph1 “P5”: 2 x 15 kW @ -25 ˚C
(in construction)
TRACI V1 (2/2)
TRACI V2 (3/3)
TRACI V3 (1/4)
PLC-based logic
Touch-screen
New pump(s)
Improved piping design
Portable laboratory units:
~100 W @ -30 ˚C
High power and low temperature systems for CMS and Atlas inner detector upgrades

## Slide 13: CO2 cooling projects in LHC
27 km
Ca. 100m
LHC
VELO detector: 1.5 kW@-30°C
(Running successfully since 2007)
Atlas IBL: 1.5 kW@-40°C
(Operational 2013)
CMS pixel: 15 kW@-20°C
(Operational 2014)

## Slide 14: LHCb-Velo Thermal Control System (LHCb-VTCS)
LHCb experimental cavern
Evaporator
Passive tubing only
Cooling Plant
All active hardware
Transfer tube
Concentric assembly
Cooling capacity: 1.5 kW@-30°C

## Slide 15: VTCS Evaporator

## Slide 16: The 1st CO2 cooling system in Space!
A CO2 cooling system for Alpha Magnetic Spectrometer (AMS) Tracker Detector on the International Space station (ISS)
CO2 cooling radiator
AMS on the ISS
AMS in the Shuttle (STS-134, May 2011)

## Slide 17: AMS-Tracker Thermal Control System (AMS-TTCS)
Wake radiator with condensers
Ram radiator with condensers
Cooling system component boxes
(1 redundant)
150 Watt detector with evaporator rings
Primary cooling not needed in space as environment is cold. Direct radiation to space
17

## Slide 18: ATLAS IBL: A new 1st layer around a reduced beam pipe
IBL pixel sensors
IBL Carbon stave with cooling pipe
IBL Stave
IBL an extra pixel layer
Component (32 per stave) | Power (W/unit) | Power (W/stave)
FEI4 chip | 1.12 | 35.84
Pixel sensor (after irradiation) | 0.68 | 21.61
Stave flex | 0.17 | 5.38
Type 1 cables | 0.17 | 5.38
Total per stave |  | 68.21
Total for 14 staves |  | 954.94
Cooling temperature required: <-35°C

## Slide 19: The IBL cooling loops
Manifold box in S5
Splitter box
PP1 connectors
Splitter box in IDEP
1 round trip = 1 loop = 31m
Flex line routing in IDEP
Evaporator tubes in staves 1.5mm
7 miniature vacuum insulated flexible cooling lines (<18mm)

## Slide 20: Cooling plants in USA-15
CO
2
Freon
CO
2
Freon
Control
IBL has 2 redundant CO2 systems, in case of failure it swaps transparent to the other system. Detector is minimal affected (small temperature fluctuation)
System A
System B
Controls
Accumulator
Front view
Rear view
Transfer line

## Slide 21: CMS upgrade pixel cooling system
Replacement and upgrade of current pixel detector
15kW @ -20ºC
Very long serial lines with relative high heat flux
B-PIX (Barrel)
F-PIX
(Forward)

## Slide 22: CMS pixel plant

## Slide 23: Practicum
Let’s build a CO2 cooling machine!!!

## Slide 24: Blow system
+
-
-

## Slide 26
Temperature (C) | Pressure (bar) | Density (kg/m3) | Enthalpy liquid (J/g) | Enthalpy gas (J/g) | Latent heat (J/g) | Joule-Thomson (K/bar) | VQ from 20'C expansion | Max Heatload @ 0.5 g/s | Max Heatload @ 1 g/s | Max Heatload @ 1.5 g/s | Max Heatload @ 2 g/s | Max Heatload @ 2.5 g/s
-53.115 | 6 | 1166 | 86.796 | 431.65 | 344.854 | 2.5073 | 49.55% | 86.99 | 173.98 | 260.97 | 347.96 | 434.95
-49.369 | 7 | 1152.2 | 94.191 | 432.87 | 338.679 | 2.3962 | 48.27% | 87.6 | 175.2 | 262.8 | 350.4 | 438
-46.005 | 8 | 1139.6 | 100.87 | 433.86 | 332.99 | 2.3031 | 47.09% | 88.095 | 176.19 | 264.285 | 352.38 | 440.475
-42.941 | 9 | 1127.9 | 106.99 | 434.65 | 327.66 | 2.2235 | 45.99% | 88.49 | 176.98 | 265.47 | 353.96 | 442.45
-40.122 | 10 | 1116.9 | 112.66 | 435.3 | 322.64 | 2.1542 | 44.94% | 88.815 | 177.63 | 266.445 | 355.26 | 444.075
-37.504 | 11 | 1106.5 | 117.95 | 435.81 | 317.86 | 2.0929 | 43.96% | 89.07 | 178.14 | 267.21 | 356.28 | 445.35
-35.057 | 12 | 1096.7 | 122.93 | 436.22 | 313.29 | 2.0381 | 43.01% | 89.275 | 178.55 | 267.825 | 357.1 | 446.375
-32.757 | 13 | 1087.2 | 127.65 | 436.54 | 308.89 | 1.9886 | 42.09% | 89.435 | 178.87 | 268.305 | 357.74 | 447.175
-30.583 | 14 | 1078.2 | 132.13 | 436.77 | 304.64 | 1.9436 | 41.21% | 89.55 | 179.1 | 268.65 | 358.2 | 447.75
-28.521 | 15 | 1069.5 | 136.41 | 436.93 | 300.52 | 1.9023 | 40.35% | 89.63 | 179.26 | 268.89 | 358.52 | 448.15
-26.557 | 16 | 1061 | 140.52 | 437.02 | 296.5 | 1.8642 | 39.51% | 89.675 | 179.35 | 269.025 | 358.7 | 448.375
-24.682 | 17 | 1052.8 | 144.46 | 437.06 | 292.6 | 1.8288 | 38.69% | 89.695 | 179.39 | 269.085 | 358.78 | 448.475
-22.886 | 18 | 1044.8 | 148.27 | 437.04 | 288.77 | 1.7957 | 37.88% | 89.685 | 179.37 | 269.055 | 358.74 | 448.425
-21.162 | 19 | 1037 | 151.95 | 436.97 | 285.02 | 1.7646 | 37.09% | 89.65 | 179.3 | 268.95 | 358.6 | 448.25
-19.503 | 20 | 1029.4 | 155.52 | 436.85 | 281.33 | 1.7353 | 36.31% | 89.59 | 179.18 | 268.77 | 358.36 | 447.95
-17.903 | 21 | 1021.9 | 158.99 | 436.69 | 277.7 | 1.7075 | 35.53% | 89.51 | 179.02 | 268.53 | 358.04 | 447.55
-16.359 | 22 | 1014.5 | 162.36 | 436.49 | 274.13 | 1.6811 | 34.77% | 89.41 | 178.82 | 268.23 | 357.64 | 447.05
-14.864 | 23 | 1007.3 | 165.64 | 436.25 | 270.61 | 1.656 | 34.01% | 89.29 | 178.58 | 267.87 | 357.16 | 446.45
-13.417 | 24 | 1000.2 | 168.85 | 435.97 | 267.12 | 1.6321 | 33.25% | 89.15 | 178.3 | 267.45 | 356.6 | 445.75
-12.013 | 25 | 993.2 | 171.98 | 435.66 | 263.68 | 1.6091 | 32.50% | 88.995 | 177.99 | 266.985 | 355.98 | 444.975
-10.65 | 26 | 986.27 | 175.05 | 435.32 | 260.27 | 1.5872 | 31.74% | 88.825 | 177.65 | 266.475 | 355.3 | 444.125
-9.3243 | 27 | 979.42 | 178.06 | 434.94 | 256.88 | 1.5661 | 30.99% | 88.635 | 177.27 | 265.905 | 354.54 | 443.175
-8.0342 | 28 | 972.64 | 181.01 | 434.53 | 253.52 | 1.5457 | 30.24% | 88.43 | 176.86 | 265.29 | 353.72 | 442.15
-6.7775 | 29 | 965.92 | 183.9 | 434.08 | 250.18 | 1.5261 | 29.49% | 88.205 | 176.41 | 264.615 | 352.82 | 441.025
-5.5521 | 30 | 959.25 | 186.75 | 433.61 | 246.86 | 1.5072 | 28.73% | 87.97 | 175.94 | 263.91 | 351.88 | 439.85
-4.3564 | 31 | 952.63 | 189.56 | 433.11 | 243.55 | 1.4888 | 27.97% | 87.72 | 175.44 | 263.16 | 350.88 | 438.6
-3.1886 | 32 | 946.05 | 192.32 | 432.57 | 240.25 | 1.471 | 27.20% | 87.45 | 174.9 | 262.35 | 349.8 | 437.25
-2.0474 | 33 | 939.5 | 195.05 | 432.01 | 236.96 | 1.4537 | 26.43% | 87.17 | 174.34 | 261.51 | 348.68 | 435.85
-0.93132 | 34 | 932.97 | 197.74 | 431.42 | 233.68 | 1.4368 | 25.65% | 86.875 | 173.75 | 260.625 | 347.5 | 434.375
0.16082 | 35 | 926.47 | 200.39 | 430.8 | 230.41 | 1.4203 | 24.86% | 86.565 | 173.13 | 259.695 | 346.26 | 432.825
1.2302 | 36 | 919.98 | 203.02 | 430.15 | 227.13 | 1.4041 | 24.06% | 86.24 | 172.48 | 258.72 | 344.96 | 431.2
2.2778 | 37 | 913.5 | 205.62 | 429.47 | 223.85 | 1.3883 | 23.25% | 85.9 | 171.8 | 257.7 | 343.6 | 429.5

## Slide 27
Temperature (C) | Pressure (bar) | Density (kg/m3) | Enthalpy liquid (J/g) | Enthalpy gas (J/g) | Latent heat (J/g) | Joule-Thomson (K/bar) | VQ from 20'C expansion | Max Heatload @ 0.5 g/s | Max Heatload @ 1 g/s | Max Heatload @ 1.5 g/s | Max Heatload @ 2 g/s | Max Heatload @ 2.5 g/s
3.3047 | 38 | 907.02 | 208.19 | 428.76 | 220.57 | 1.3727 | 22.43% | 85.545 | 171.09 | 256.635 | 342.18 | 427.725
4.3117 | 39 | 900.54 | 210.74 | 428.02 | 217.28 | 1.3574 | 21.60% | 85.175 | 170.35 | 255.525 | 340.7 | 425.875
5.2997 | 40 | 894.05 | 213.27 | 427.25 | 213.98 | 1.3423 | 20.75% | 84.79 | 169.58 | 254.37 | 339.16 | 423.95
6.2695 | 41 | 887.54 | 215.78 | 426.44 | 210.66 | 1.3275 | 19.89% | 84.385 | 168.77 | 253.155 | 337.54 | 421.925
7.2218 | 42 | 881.02 | 218.28 | 425.61 | 207.33 | 1.3127 | 19.00% | 83.97 | 167.94 | 251.91 | 335.88 | 419.85
8.1574 | 43 | 874.47 | 220.75 | 424.74 | 203.99 | 1.2981 | 18.10% | 83.535 | 167.07 | 250.605 | 334.14 | 417.675
9.0767 | 44 | 867.89 | 223.22 | 423.84 | 200.62 | 1.2836 | 17.17% | 83.085 | 166.17 | 249.255 | 332.34 | 415.425
9.9804 | 45 | 861.27 | 225.68 | 422.9 | 197.22 | 1.2692 | 16.22% | 82.615 | 165.23 | 247.845 | 330.46 | 413.075
10.869 | 46 | 854.6 | 228.12 | 421.93 | 193.81 | 1.2548 | 15.25% | 82.13 | 164.26 | 246.39 | 328.52 | 410.65
11.743 | 47 | 847.88 | 230.56 | 420.92 | 190.36 | 1.2405 | 14.24% | 81.625 | 163.25 | 244.875 | 326.5 | 408.125
12.604 | 48 | 841.1 | 233 | 419.88 | 186.88 | 1.2261 | 13.20% | 81.105 | 162.21 | 243.315 | 324.42 | 405.525
13.45 | 49 | 834.25 | 235.43 | 418.79 | 183.36 | 1.2118 | 12.13% | 80.56 | 161.12 | 241.68 | 322.24 | 402.8
14.284 | 50 | 827.32 | 237.87 | 417.66 | 179.79 | 1.1974 | 11.01% | 79.995 | 159.99 | 239.985 | 319.98 | 399.975
15.105 | 51 | 820.3 | 240.3 | 416.48 | 176.18 | 1.1829 | 9.86% | 79.405 | 158.81 | 238.215 | 317.62 | 397.025
15.913 | 52 | 813.18 | 242.74 | 415.26 | 172.52 | 1.1682 | 8.65% | 78.795 | 157.59 | 236.385 | 315.18 | 393.975
16.71 | 53 | 805.96 | 245.19 | 413.99 | 168.8 | 1.1535 | 7.39% | 78.16 | 156.32 | 234.48 | 312.64 | 390.8
17.495 | 54 | 798.61 | 247.65 | 412.66 | 165.01 | 1.1386 | 6.07% | 77.495 | 154.99 | 232.485 | 309.98 | 387.475
18.269 | 55 | 791.13 | 250.13 | 411.28 | 161.15 | 1.1234 | 4.68% | 76.805 | 153.61 | 230.415 | 307.22 | 384.025
19.031 | 56 | 783.49 | 252.62 | 409.83 | 157.21 | 1.108 | 3.21% | 76.08 | 152.16 | 228.24 | 304.32 | 380.4
19.783 | 57 | 775.69 | 255.13 | 408.32 | 153.19 | 1.0923 | 1.66% | 75.325 | 150.65 | 225.975 | 301.3 | 376.625
20.525 | 58 | 767.69 | 257.67 | 406.73 | 149.06 | 1.0762 | 0.00% | 74.53 | 149.06 | 223.59 | 298.12 | 372.65
21.256 | 59 | 759.48 | 260.24 | 405.07 | 144.83 | 1.0598 |  |  |  |  |  | 
21.978 | 60 | 751.03 | 262.85 | 403.32 | 140.47 | 1.0429 |  |  |  |  |  | 
22.69 | 61 | 742.31 | 265.49 | 401.47 | 135.98 | 1.0254 |  |  |  |  |  | 
23.392 | 62 | 733.26 | 268.19 | 399.52 | 131.33 | 1.0074 |  |  |  |  |  | 
24.084 | 63 | 723.84 | 270.96 | 397.44 | 126.48 | 0.98865 |  |  |  |  |  | 
24.768 | 64 | 713.99 | 273.79 | 395.22 | 121.43 | 0.9691 |  |  |  |  |  | 
25.442 | 65 | 703.62 | 276.72 | 392.84 | 116.12 | 0.94861 |  |  |  |  |  | 
26.108 | 66 | 692.62 | 279.76 | 390.27 | 110.51 | 0.92701 |  |  |  |  |  | 
26.765 | 67 | 680.85 | 282.95 | 387.47 | 104.52 | 0.90405 |  |  |  |  |  | 
27.413 | 68 | 668.1 | 286.32 | 384.37 | 98.05 | 0.87939 |  |  |  |  |  | 
28.052 | 69 | 654.08 | 289.93 | 380.9 | 90.97 | 0.85253 |  |  |  |  |  | 
28.683 | 70 | 638.31 | 293.88 | 376.91 | 83.03 | 0.82261 |  |  |  |  |  |