## Slide 1: HiLumi Cryogenics, Progress highlights and perspectives
Serge Claudet,
On behalf of the Cryogenic project team
October 14th 2019

## Slide 2
Table of contents
Introduction
P1/P5, interfaces revisited (IT, D2, DF’s, CC)
P1/P5, QXL cryoline integrated
P1/P5, process studies – controls architecture
P4 upgrade
Summary

## Slide 3: HL-LHC cryogenic upgrade
+
P1-P5: 2 new cryoplants (~15 kW @ 4.5 K incl. ~3 kW @ 1.8 K ) and 2 x 750m cryo-distribution for high-luminosity insertions
P4: upgrade (+2 kW @ 4.5 K) of an existing LHC 18 kW @ 4.5K cryoplant
SPS-BA6: SRF test facility with beam primarily for Crab-Cavities
SPS-BA6
Other test facilities related activities not reported here
P1/P5: Provide adequate cooling for this
14Oct'19

## Slide 4: Heat loads mechanisms - Cross Section
14Oct'19

## Slide 5: Heat transfer measurements in Nb3Sn stacks
Inter layer DT
Characterisation of material properties
Porosity to He
14Oct'19

## Slide 6: Beam-Screen thermal behaviour
2+ years of elementary and complete tests done at cryolab, now completed
14Oct'19

## Slide 7: Revised Process & Flow diagram
1) The electrical heater could be moved to a lower radiation area  main reason
Lower radiation region
2) Separate supplies allow separate CV at inlet for better flow control  positive effect
Splitting valves
Reasons
14Oct'19

## Slide 8
IT+D1: LD’ lines for transients
Horizontal reference
P1
OUTLET
OUTLET
Emptying
Quench
Cool-down
(Re)Filling
Emptying
Quench
Cool-down
(Re)Filling
Horizontal reference
P5
OUTLET
OUTLET
Cool-down
(Re)Filling
Emptying
Quench
Emptying
Quench
Cool-down
(Re)Filling
14Oct'19

## Slide 9: D2 heat exchanger
Studies, procurement and validations tests under collaboration with CEA-SBT Grenoble
Performance validated @CEA Sept’19
13.5m
Not sensitive to slope, adapted for stand-alone magnets, up to 70W@2K ?
14Oct'19

## Slide 10: Cold powering, cryogenic aspects
Being studied and defined for warm extremity with leads
Defined with a baseline for cold extremity,
14Oct'19

## Slide 11: New CC warm-up proposal
The objective is to warm-up the CC using warm helium from thermal shield at 60 K
The circuit to this purpose would be
Eh  E’h  CS  CC  XB  LD  D
The Warm-up control valve will regulate the flow in order to perform the warm-up in a controled way
The proposed warm-up configuration must cope with the existing safety scheme
Safety valve
Burst disk
Warm-up
Control valve
Control valve
To Header D
Valve type | CV to Header D | SV to atmosphere | BD to atmosphere
Opening [bar a] | 1.5 | 1.7 | 2.1
Kv [m3/h] | t.b.d. | - | -
Aperture [mm] | - | < 20 | 100
Tolerance [%] | +0% -10% | +10% -10% | +10% -0%
Remarks | Helium recovery | First protection | Extreme protection
New simplified arrangement for independent warm-up now ready for decision
14Oct'19

## Slide 12
Table of contents
Introduction
P1/P5, interfaces revisited (IT, D2, DF’s, CC)
P1/P5, QXL cryoline integrated
P1/P5, process studies – controls architecture
P4 upgrade
Summary
14Oct'19

## Slide 13: QXL cryoline headers
Typical Tunnel cross section
Marco Spitoni HL-LHC / WP9
Inner Triplet flow scheme
B
D
C
Eh
Fh
Typical QXL cross section
QXL
Users
Header Eh  Supply of thermal shield and beam screen (IT only)
Header Fh  Return of header Eh
Header C  Supply of supercritical He
Header B  Return of superfluid He (very low pressure)
Header D  Return from DFX-DFM, beam screen (D2, CC, SAMs)
Various modes:
- Nominal
- Reduced capacity
- Cool-down
- Quench
- Other transients
13

## Slide 14: QXL Cryoline sizing, and 3D model integrated !
Typical Tunnel cross section
Marco Spitoni HL-LHC / WP9
Large “B” to match pressure drop criteria
Constant outer diameter as boundary limit so far
Verifying jumper/piping interfaces with all users while progressing now in service galleries
B
D
C
Eh
Fh
Typical QXL - Service Galleries
Increased “D” to provide cold quench buffer for triplets
Reduced “B” as not impacting pressure drop
Typical QXL – LHC Tunnel
B
D
C
Eh
Fh
14Oct'19
14

## Slide 15: QXL cryoline, 3D models and integration
14Oct'19

## Slide 16
14Oct'19
An example, done for all jumper interfaces

## Slide 17: P1/P5 Cryogenic architecture
QSCG
QSVB
QSDQ
QSRG
QSDN
QSAG
QURCG
QPLG
QXL
DFHM
DFHX
QSP
GHe storage tanks
Dryer
Liquid Nitrogen tank(s)
Surface cold box
Vertical transfer line
Quench tank
Surface piping
Warm compressor station
DSHX
DSHM
DSL
Q1
Q2b
Q3
CP
D1
D2
CC
CC
Q4
Q5
Q6
HRL
QRP
QPP
SHE
SHM
SD
US
SLN
SLN
Q2a
Surface
Shaft
Underground
15 kW equivalent at 4.5 K, including 3 kW at 1.8 K
Cold compressors box
QUIG
Interconnection box
UR
UL
DFBL
(existing)
CC
CC
LHC tunnel
DFX
DFM
14Oct'19

## Slide 18: From cooling requirements to Refrigeration capacity and process
Load @
4.5-20K
Load @
40-60K
Load @
4.5-300K
Load @
1.9-2K
LC
HX
40 K
60 K
4,5 K
20 K
300 K
4 K
D
C
E
B
F
QSRG
QURCG
QSCG
QPLG
Obvious need for 15mbar header (1.8K cold source), no special need for 4.5K loads
Process options now under study
14Oct'19

## Slide 19: Managing dynamic loads
J to Hepress
J to Hepress
B
C
Refrigerator
Cold Compressor
J to Hesub
HEX
Magnet Cryostat
Cryo-distribution
Z max
Z min
Heater
Beam on
Beam off
m’ = CC driven
#1: Acceleration
#3: Lumi ramp
#2: Pre-load + active controls
14Oct'19

## Slide 20
HL-LHC cryogenic “control” principles
Instrumentation
=> Racks-Electronics
=> Controls

## Slide 21: Project plans Refrigeration-Distribution
Interfaces to be frozen by end 2020
Used now to discuss for LS3 (ready to install, P1 w.r.t P5)
-
+
Today
UL’s available
UR’s available
LS3
14Oct'19

## Slide 22
Table of contents
Introduction
P1/P5, interfaces revisited (IT, D2, DF’s, CC)
P1/P5, QXL cryoline integrated
P1/P5, process studies – controls architecture
P4 upgrade
Summary
14Oct'19

## Slide 23: Upgrade of Helium Refrigerator at LHC Point 4 for HL-LHC – Upper and Lower Cold Boxes
Upper CB: 4 TU’s
Lower CB: 4 TU’s
Principle of the capacity upgrade: to replace 8 turbines by new type (more efficient)
This requires exchange of turbine housings & instrumentation
Surface
Shaft
Cavern
Cut view of existing cold box
New turbine housings and instrumentation
Spares and repairs: to ensure availability as for all helium refrigerators
Site works: Q4-2019
Commissioning: Q2-2020
(FC Dec’18)
14Oct'19

## Slide 24: P4 lower cold box, from inner piping to new turbine interface
Next: work on-site to start end oct’19
Towards modified new inner parts into “old” housing
Linde 12-18kW Lower Cold-Box
3D model of internal piping
(picture 25 yrs ago)
Heat exchangers
Turbines
Cryolines interfaces
LHe phase separator
Valve actuators
14Oct'19

## Slide 25: Summary
P1/P5 in 2019:
  Final definition of interfaces with superconducting sub-systems
  The HiLumi cryoline (QXL) has been sized and integrated
  Process studies have started, together with management of dynamic heat loads
  Instrumentation racks and controls architecture being studied
2020: Global review of heat loads foreseen to allow freezing requirements and proceed with procurement
P4 upgrade is well advanced, on track for tests in Q2-2020
14Oct'19

## Slide 26: WP9 organisation and roles
Coordination: Serge Claudet, Rob Van Weelderen
Quality, documentation, project management: Antonio Perin + Sigrid Knoops*
Magnet cooling requirements: Rob Van Weelderen + K. Puthran
Crab cavities cooling requirements: Krzysztof Brodzinski
Heat Load management: Antonio Perin + M. Spitoni
General process overview: Udo Wagner + Vanessa Gahier + Benjamin Bradu
3D models and integration: Jos Metselaar (+ designers)
Instrumentation & controls: so far CRG/CE-CI experts
P4-RF and P1-P5
  Refrigeration: Emmanuel Monneret (Sep’17)
  Cryodistribution: Michele Sisti (Jun’17)
  Cryogenic infrastructure: Gérard Ferlin (Jul’19)
SPS-BA6:
  Refrigeration: Laurent Delprat
  Cryodistribution: Krzysztof Brodzinski + Hendrie Derking
  Infrastructure: Jos Metselaar + O. Pirotte
Re-inforced 2019
Part time contributors during LS2, but valuable help expected from experienced colleagues
Done!
Consolidations: S. Claudet + Jos Metselaar
14Oct'19