## Slide 1: HL-LHC WP9 Cryogenics, an introduction for this Functional analysis
S. Claudet, 09May’19
(HiLumi – CRG internal review)

## Slide 2: Goal of this mini series of meetings
For the HiLumi cryogenics at P1/P5, we have now completed the series of expected heat loads, flow diagrams and preliminary sizing of the QXL headers (QXL: Cryoline for HiLumi). With specificities due to Nb3Sn magnets and higher pulsed heat loads than for LHC, we would like to consolidate our approach with your help.
Our goal is to evaluate possible operation modes, control techniques, instrumentation for measurements (range, accuracy) and actuators, propose alternative schemes if advantageous and justified
We believe it is now time to present the status of our studies to a larger audience in the cryo group, and get feedback from experienced colleagues in functional analysis and control techniques. As validated at pilotage last autumn and following similar work recently done for QXL sizing, we would propose to start a small series of meetings on this topic.
The concerned cooling loops would be for users: 11T, IT+D1, D2, sc links, CC
We could consider: introduction and presentation of reference so far, then parametric studies done so far for all headers with comments/discussion, then further studies that could allow to update and consolidate the baseline.
The final deliverable should be a joint recommendation to go from P&F_Diagrams to P&I_Diagrams, instrumentation main characteristics and control techniques envisaged.
The reference documentation so far:
- Preliminary heat loads estimates: EDMS-1610730
- Process & Flow Diagrams and typical QXL cross sections will be presented
- Functional requirements for heat extraction, CERN-ACC-Note-2019 being finalised
For the organisation of these meetings, we will prepare ad-hoc indico sites, call for meeting and prepare executive minutes of meetings
Participants:
- HL-Cryo: Marco Spitoni, Michele Sisti, Emmanuel Monneret, Krzysztof Brodzinski, Antono Perin, Rob van Weelderen, Serge Claudet
- CRG: Benjamin Bradu, Krzysztof Brodzinski, Laurent Delprat, Gérard Ferlin, Vanessa Gahier, Udo Wagner, Marco Pezzetti
- Convenors: Michele Sisti, Serge Claudet
Thursdays 10h30-12h.
To be complete, this series will be complemented with another one: global instrumentation and control architecture.
Circuits, Actuators, Sensors,
Control Technics
! Dynamics ! - ! Radiation !

## Slide 3: Agenda
Next meeting to be defined at the end, depending on needs and outcome of this meeting

## Slide 4: P1/P5 Cryogenic architecture
QSCG
QSVB
QSDQ
QSRG
QSDN
QSAG
QURCG
QPLG
QXL
DFHM
DFHX
QSP
GHe storage tanks
Dryer
Liquid Nitrogen tank(s)
Surface cold box
Vertical transfer line
Quench tank
Surface piping
Warm compressor station
DSHX
DSHM
DSL
Q1
Q2b
Q3
CP
D1
D2
CC
CC
Q4
Q5
Q6
HRL
QRP
QPP
SHE
SHM
SD
US
SLN
SLN
Q2a
Surface
Shaft
Underground
LHC tunnel
18 kW equivalent at 4.5 K, including 3 kW at 1.8 K
Cold compressors box
QUIG
Interconnection box
UR
UL
DFBL
(existing)
Very limited impact identified for QXL headers

## Slide 5: Inner Triplets Cooling (LHC vs HL-LHC)
cryostat
cryostat
LHC
HL-LHC
Fermilab
Nb-Ti + single cooling channel at 1.8K
Tungsten shielding
CERN
Beam Screen
Cold Mass
Assembly (IT.R5)
Nb-3Sn + double cooling channel at 1.8K
Notes: 5

## Slide 6: HL-LHC: heat loads on triplets
Based on data from F. Cerutti at 4th HiLumi annual meeting at KEK
Highly “luminosity driven”

## Slide 7
1st Evaluation of Heat Loads
1000 W
1200 W

## Slide 8
(slope dependent)

## Slide 10
(pre-load?)
Consideration during LHC design phase: (driven by Cold Compressors dynamic)
Advanced controls, Feed forward
Classic (PID) tuning

## Slide 11: Introduction to dynamic effects, main parameters
Injection
(~Static losses)
Nominal
(mode)
Installed mode
(~150% Nom)
x2
Magnet ramping effect covered by margin in total capacity
He buffering
Maximum flow
Flow acceleration
IT-2545/LHC/LHC, 1.8K Units

## Slide 12: Introduction to heat loads per origin
Magnet
Beam
?
Qualitative illustration (with not too bad orders of magnitude)
=> This will deserve specific strategy

## Slide 13: WG1, QXL headers
Typical Tunnel cross section
Marco Spitoni HL-LHC / WP9
Inner Triplet flow scheme
B
D
C
Eh
Fh
Typical QXL cross section
QXL
Users
Header Eh  Supply of thermal shield and beam screen (IT only)
Header Fh  Return of header Eh
Header C  Supply of supercritical He
Header B  Return of superfluid He (very low pressure)
Header D  Return from DFX-DFM, beam screen (D2, CC, SAMs)
Various modes:
- Nominal
- Reduced capacity
- Cool-down
- Quench
- Other transients
13

## Slide 14: WG2, Summary results
Marco Spitoni HL-LHC / WP9
Thermal shield
(Eh - Fh)
Header B
Header C
Header D
Baseline HL-LHC
(DN)
50 - 65
DN 40 - DN 50
(ΔP reasons)
250
DN 200 @ LSS_
(encumbrance)
80
DN 50
(ΔP reasons)
DN 100/125 ?
(damping reasons)
DN 300 @ caverns?
(damping reasons)
125
Could be decreased
(ok for ΔP)
(not ok quench)
DN 200 @ LSS_
(quench buffer)
Higher
DN
Lower
DN
No changes for the time being
Not yet started
Directly affects
QXL vacuum jacket
Study started
Maximum increase
 to be investigated
LHC
(mm)
80 - 80
267
100
150
DN 65
(conservative)
14
On-going work on damping effects for C (close to a baseline) and B (not much hope with “short” QXL w.r.t QRL 180m3)

## Slide 15: Project plans Refrigeration-Distribution
-
+

## Slide 16: Complements (if needed)

## Slide 18: QXL Cryoline integration

## Slide 19: HL-LHC refrigeration capacity at Points 1 & 5
Temperature level | Cooling circuit | Specific heat load [W/m] (Static) | Capacity* / Point |  | Dynamic range
40-60 K | IT beam screen | 16 (0) | 3.2 kW | 13 kW | ~1.3
 | Thermal shield | 6 (6) | 3.6 kW |  | 
 | Crab cavity | - | 6 kW |  | 
20-300 K | Current lead & SC link | - | 40 g/s | 40 g/s | ~2
4.5-20 K | MS beam screen | 2 (0.1) | 0.1 kW | 0.1 kW | ~20
1.9 – 2 K | Cold-mass (1.9 K) | 14 (0.35) | 2.6 kW | 3 kW | ~10
 | Crab-cavity (2 K) | - | 0.4 kW |  | 
*: Including uncertainty and design capacity factor
Preliminary global values
About 18kW eq. @ 4.5K, including 3kW @ 1.8K

## Slide 20: Cooling P1/P5 SAM’s
Q6
Q5
Q4
D2
LHC
HL
Present limit for QRL/QXL
Access / safety / sectorisation ?
Powering from existing RR & DFBL, corresponding cooling of DFBL and SAM’s to be with same origin
(QRL or QXL but not mixed)
Q4 and Q5 possibly with remote alignment, compatible with QRL ?
3D models to be implemented and then integrated (Q2-2018 for CRG)
NEW Jan’18
Q4-Q5 could remain at 4.5K (already the case for Q6),
and moved towards the arc by 10-11m
Return Module
Return Module
QRL
QXL
View from integration views DB

## Slide 21: Possible modes and implications, as identified so far for HiLumi
Ultimate Luminosity (HL)
Nominal Luminosity (HL)
Nominal Luminosity (LHC)
Low Luminosity / Intensity
. Powering conditions to 7TeV, (maybe pilots or few bunches)
Injection stand-by (He preservation in magnets, ELQA, maybe pilots or few bunches at injection)
Magnets @20K
=> Junction Module and bridge between WRL’s recommended
=> Corresponding cooling capacities and impact on size/cost/volume to be further investigated
Decreasing requirements in cooling capacity
LHC
HL
=> The maximum reasonably possible
Mandatory (few wks)
Desired (1 wk)
Bonus (only 1st year)
WRL
Junction Module QRL-QXL