## Slide 1: HL-LHC WP9 Cryogenics, an introduction for this Controls & Instrumentation Architecture wg
S. Claudet, 16May’19
(HiLumi – CRG internal review)

## Slide 2: Goal of this mini series of meetings
For the HiLumi cryogenics at P1/P5, we have now completed the series of expected heat loads, flow diagrams and preliminary sizing of the QXL headers (QXL: Cryoline for HiLumi). We would like to complement this work with a similar one for controls.
Our goal is to evaluate possible control architectures, interfaces with existing ones, and typical needs for racks and cables
As validated at pilotage last autumn and following similar work recently done for QXL sizing, we would propose to start a small series of meetings on this topic with specialised and experienced collegues in the group.
We could consider: introduction and presentation of reference so far for HiLumi cryogenics from our side, and LHC controls architecture from your side.
Discussion, studies for possible scheme for instrumentation and controls of HiLumi cryogenics.
A summary document with schemes and list should be the final deliverable.
For the organisation of these meetings, we will prepare ad-hoc indico sites, call for meeting and prepare executive minutes of meetings
Participants:
- HL-Cryo: Marco Spitoni, Michele Sisti, Emmanuel Monneret, Krzysztof Brodzinski, Serge Claudet
- CRG: Nikolaos Trikoupis, Juan Casas-Cubillos, Czeslaw Fluder, Marco Pezzetti, Benjamin Bradu
- Convenors: Michele Sisti, Serge Claudet
We would propose to use the slot on Thursdays 10h30-12h, tentatively and if nobody objects, we could start May 16th.
Looking forward to meeting you and getting your feedback!
Wg2: Functional Analysis
Circuits, Actuators, Sensors,
Control Technics
! Dynamics ! - ! Radiation !
Wg1: Cryoline QXL sizing
Done

## Slide 3: Agenda
Next meeting to be defined at the end, depending on needs and outcome of this meeting
https://indico.cern.ch/category/10932/

## Slide 4: High Luminosity Large Hadron Collider (HL-LHC)
10/04/2019
Main consequences
New accelerator components
Higher beam induced heat loads
Peak luminosity 
Integrated luminosity 
Main objective  Higher collision rate
By increasing the number of bunches
By decreasing the bunch’s size
Two new refrigerators at
P1 ad P5
(higher heat load)
Inner Triplet (@ 1.9K)
300 W  1000 W
15 g/s  50 g/s
No way that the existing cryo-plants could deliver the additional capacity being 3.3 km away (both sides)
4

## Slide 5: Inner Triplets Cooling (LHC vs HL-LHC)
cryostat
cryostat
LHC
HL-LHC
Fermilab
Nb-Ti + single cooling channel at 1.8K
Tungsten shielding
CERN
Beam Screen
Cold Mass
Assembly (IT.R5)
Nb-3Sn + double cooling channel at 1.8K
Notes: 5

## Slide 6: INTERFACES identification and definition
D.Berkowitz for HL-LHC WP9 – Nov17 – EDMS 1865871 v.0.9.
A large variety of cold masses, beam-screens and sc-links
Specific study done
=> Will be kept with arc/QRL
Close to validate technical choices in order to finalise design
D2 cooling heat exchanger collaboration with CEA-SBT
SC Link = 60 m
Un-shielded cryostats validated
Thermal behaviour of tungsten beam-screen validated at Cryolab,
now looking for off-design modes
3D models for Cryo started this year!
Heat extraction

## Slide 7: P1/P5 Cryogenic architecture
QSCG
QSVB
QSDQ
QSRG
QSDN
QSAG
QURCG
QPLG
QXL
DFHM
DFHX
QSP
GHe storage tanks
Dryer
Liquid Nitrogen tank(s)
Surface cold box
Vertical transfer line
Quench tank
Surface piping
Warm compressor station
DSHX
DSHM
DSL
Q1
Q2b
Q3
CP
D1
D2
CC
CC
Q4
Q5
Q6
HRL
QRP
QPP
SHE
SHM
SD
US
SLN
SLN
Q2a
Surface
Shaft
Underground
LHC tunnel
18 kW equivalent at 4.5 K, including 3 kW at 1.8 K
Cold compressors box
QUIG
Interconnection box
UR
UL
DFBL
(existing)
Very limited impact identified for QXL headers

## Slide 8: Cryo-distribution reference
IT-D1
D2
CC
QRL-QXL
Reference established, to be optimised considering project requirements and CRG expertise

## Slide 9: Junction module QRL-QXL
4.0 m
3.5 m
4.5 m
It should fit within 12m
Work on-going

## Slide 10: Cooling P1/P5 SAM’s
Q6
Q5
Q4
D2
LHC
HL
Present limit for QRL/QXL
Access / safety / sectorisation ?
Powering from existing RR & DFBL, corresponding cooling of DFBL and SAM’s to be with same origin
(QRL or QXL but not mixed)
Q4 and Q5 possibly with remote alignment, compatible with QRL ?
3D models to be implemented and then integrated (Q2-2018 for CRG)
NEW Jan’18
Q4-Q5 could remain at 4.5K (already the case for Q6),
and moved towards the arc by 10-11m
Return Module
Return Module
QRL
QXL
View from integration views DB

## Slide 11: Possible modes and implications, as identified so far for HiLumi
Ultimate Luminosity (HL)
Nominal Luminosity (HL)
Nominal Luminosity (LHC)
Low Luminosity / Intensity
. Powering conditions to 7TeV, (maybe pilots or few bunches)
Injection stand-by (He preservation in magnets, ELQA, maybe pilots or few bunches at injection)
Magnets @20K
=> Junction Module and bridge between WRL’s recommended
=> Corresponding cooling capacities and impact on size/cost/volume to be further investigated
Decreasing requirements in cooling capacity
LHC
HL
=> The maximum reasonably possible
Mandatory (few wks)
Desired (1 wk)
Bonus (only 1st year)
WRL
Junction Module QRL-QXL

## Slide 12: QXL Cryoline integration

## Slide 13: HL-LHC refrigeration capacity at Points 1 & 5
Temperature level | Cooling circuit | Specific heat load [W/m] (Static) | Capacity* / Point |  | Dynamic range
40-60 K | IT beam screen | 16 (0) | 3.2 kW | 13 kW | ~1.3
 | Thermal shield | 6 (6) | 3.6 kW |  | 
 | Crab cavity | - | 6 kW |  | 
20-300 K | Current lead & SC link | - | 40 g/s | 40 g/s | ~2
4.5-20 K | MS beam screen | 2 (0.1) | 0.1 kW | 0.1 kW | ~20
1.9 – 2 K | Cold-mass (1.9 K) | 14 (0.35) | 2.6 kW | 3 kW | ~10
 | Crab-cavity (2 K) | - | 0.4 kW |  | 
*: Including uncertainty and design capacity factor
Preliminary global values
About 18kW eq. @ 4.5K, including 3kW @ 1.8K

## Slide 14: HL-LHC: heat loads on triplets
Based on data from F. Cerutti at 4th HiLumi annual meeting at KEK
Highly “luminosity driven”
LHC_ARC_Cells
LHC_Triplets_P1/P5

## Slide 15: Introduction to dynamic effects, main parameters
Injection
(~Static losses)
Nominal
(mode)
Installed mode
(~150% Nom)
x2
Magnet ramping effect covered by margin in total capacity
He buffering
Maximum flow
Flow acceleration
IT-2545/LHC/LHC, 1.8K Units

## Slide 16: Project plans Refrigeration-Distribution
From WP-Central vision to project engineer ownership
without change for important milestones
Soon ready to discuss LS3 (ready to install, P1 w.r.t P5)
-
+

## Slide 17: Project plans Refrigeration-Distribution
To be operated for QXL tests at cold, and LSS commissioning
-
-
-
!
!
From WP-Central vision to project engineer ownership
With moderate anticipation for tendering
Possible to anticipate delivery in 2023 (surface),
it would require to freeze heat loads at the end of 2019 (why not)
Prepared by E. Monneret

## Slide 18: WG1, QXL headers – WG2, Functional Analysis
Typical Tunnel cross section
Marco Spitoni HL-LHC / WP9
Inner Triplet flow scheme
B
D
C
Eh
Fh
Typical QXL cross section
QXL
Users
Header Eh  Supply of thermal shield and beam screen (IT only)
Header Fh  Return of header Eh
Header C  Supply of supercritical He
Header B  Return of superfluid He (very low pressure)
Header D  Return from DFX-DFM, beam screen (D2, CC, SAMs)
Various modes:
- Nominal
- Reduced capacity
- Cool-down
- Quench
- Other transients
18

## Slide 19: Goal of this mini series of meetings
For the HiLumi cryogenics at P1/P5, we have now completed the series of expected heat loads, flow diagrams and preliminary sizing of the QXL headers (QXL: Cryoline for HiLumi). We would like to complement this work with a similar one for controls.
Our goal is to evaluate possible control architectures, interfaces with existing ones,
and typical needs for racks and cables
As validated at pilotage last autumn and following similar work recently done for QXL sizing, we would propose to start a small series of meetings on this topic with specialised and experienced collegues in the group.
We could consider: introduction and presentation of reference so far for HiLumi cryogenics from our side, and LHC controls architecture from your side.
Discussion, studies for possible scheme for instrumentation and controls of HiLumi cryogenics.
A summary document with schemes and list should be the final deliverable.
For the organisation of these meetings, we will prepare ad-hoc indico sites, call for meeting and prepare executive minutes of meetings
Participants:
- HL-Cryo: Marco Spitoni, Michele Sisti, Emmanuel Monneret, Krzysztof Brodzinski, Serge Claudet
- CRG: Nikolaos Trikoupis, Juan Casas-Cubillos, Czeslaw Fluder, Marco Pezzetti, Benjamin Bradu
- Convenors: Michele Sisti, Serge Claudet
We would propose to use the slot on Thursdays 10h30-12h, tentatively and if nobody objects, we could start May 16th.
Looking forward to meeting you and getting your feedback!
WG3

## Slide 20: Complements (if needed)

## Slide 21
1st Evaluation of Heat Loads
1000 W
1200 W

## Slide 23
(slope dependent)

## Slide 25
(pre-load?)
Consideration during LHC design phase: (driven by Cold Compressors dynamic)
Advanced controls, Feed forward
Classic (PID) tuning

## Slide 26: WG2, Summary results
Marco Spitoni HL-LHC / WP9
Thermal shield
(Eh - Fh)
Header B
Header C
Header D
Baseline HL-LHC
(DN)
50 - 65
DN 40 - DN 50
(ΔP reasons)
250
DN 200 @ LSS_
(encumbrance)
80
DN 50
(ΔP reasons)
DN 100/125 ?
(damping reasons)
DN 300 @ caverns?
(damping reasons)
125
Could be decreased
(ok for ΔP)
(not ok quench)
DN 200 @ LSS_
(quench buffer)
Higher
DN
Lower
DN
No changes for the time being
Not yet started
Directly affects
QXL vacuum jacket
Study started
Maximum increase
 to be investigated
LHC
(mm)
80 - 80
267
100
150
DN 65
(conservative)
26
On-going work on damping effects for C (close to a baseline) and B (not much hope with “short” QXL w.r.t QRL 180m3)

## Slide 27: Introduction to heat loads per origin
Magnet
Beam
?
Qualitative illustration (with not too bad orders of magnitude)
=> This will deserve specific strategy