## Slide 1: Instrumentation in the DFX: Requirements and Routing Electrical Protection and Cryogenic Sensors
J. Fleiter, S. C. Hopkins, A. Ballarino
Internal Review of DFX Detailed Design, 20th June 2019 (Indico 821876)

## Slide 2: Outline
Cold Powering Instrumentation Specification
DFX Instrumentation:
  Electrical Protection of Circuits
  Cryogenics
  Feedthroughs
  Vacuum

## Slide 3: Specification
A functional specification documenting the instrumentation requirements of the Cold Powering System of the Inner Triplets has been discussed and prepared 1
  DFX instrumentation represents a subset of that specification
A draft DFX instrumentation list was presented at the DFX conceptual design review, 31st Jan 2019 2. Since then:
  No change to the voltage taps
  Addition of two heaters for the warm-up phase and four temperature sensors for monitoring the heaters
  Addition of ΔP LHe level gauge for level monitoring in LHe fountain
1 J. Fleiter, EDMS 2087413
2 J. Fleiter, DFX Instrumentation Requirements, Indico 783116

## Slide 4: Overview of Electrical Circuits
D1
CP
Q3
Q2b
Q2a
Q1
IP
Power converters
DSHx
DFHx1
DFX
DFHx2
≈80m
Service tunnel
LHC tunnel
The cold powering system of the inner triplets consists of:
  2 × 18 kA MQXF main circuit
  3 × 7 kA MQXF trims
  2 × 13 kA D1 circuit
  12 × 2 kA MCBXF circuit
A total of 19 circuit branches will be routed through the DFX:
  The DFX hosts Nb-Ti/Nb-Ti splices between Nb-Ti bus bars and the Nb-Ti extensions of the SC Link.

## Slide 5: Overview of Electrical Circuits
HTS/MgB2
Splice
Nb-Ti/Nb-Ti
Splice
MgB2/Nb-Ti
Splice
Present Scope
Each circuit branch consists of:
  SC cables
    Nb-Ti bus bar passing through the plug (~3.5m in DFX)
    Nb-Ti bus bar extension connected at the surface to the MgB2 cables (~1.5 m)
    MgB2 cable (~100 m long)
    HTS cable (~3-5 m long)
  Splices
    Nb-Ti/Nb-Ti
    MgB2/Nb-Ti
    HTS/MgB2

## Slide 6: Electrical Protection Requirements
Requirements for circuit protection were presented in the cold powering review, July 2017 1:
  Active protection of SC cables and current leads.
  Monitoring of individual splices:
    MgB2/HTS, MgB2/Nb-Ti and Nb-Ti/Nb-Ti.
  Redundancy of voltage taps.
Active protection shall be implemented with a dedicated Quench Detection/Protection System that:
  Detects any quench or detached voltage taps, and
  Triggers the discharge of the circuit.
1 A. Ballarino, Requirements for the protection of the SC links components, Indico 643197

## Slide 7: Instrumentation for Circuit Protection
Each circuit branch will be equipped with voltage taps:
  1 pair within the DFX cold mass to monitor the Nb-Ti/Nb-Ti splice
  1 pair routed via the DFX to monitor the Nb-Ti/MgB2 splice
  1 pair to protect the line inside the DFX
  1 pair to protect the Nb-Ti bus through the plug (1 wire from the DFX, 1 from the cold diode module)
  One spare for each of the above
  14 wires per circuit branch to route out from the DFX
Wire for voltage taps:
  Polyimide insulated Cu wire, AWG 26 (used for magnet instrumentation) 1
1 Axon HH2619, EDMS 2030599
Enlarge

## Slide 8: Cryogenic Requirements of the DFX
Immersion of Nb-Ti/MgB2 splices and Nb-Ti bus bars in saturated LHe bath at 1.3 bar:
  LHe level regulation required
Generate a GHe mass flow from the LHe bath to:
  Maintain the MgB2 cable assembly within the SC Link at below 17 K
  Maintain all the MgB2/HTS splices (DFH box) below 17 K
  Thermalize the cold terminal of the heat exchanger of each current lead to 50 K

## Slide 9: General Cryogenic Layout of the SC Link for the Triplets
General cryogenic instrumentation layout of SC Link elaborated with S. Claudet
Wiring of cryo instrumentation of DFX routed via the DFX feedthrough
No routing of cryo instrumentation of DFH and current leads via the DFX
 Focus on DFX in this presentation

## Slide 10: Cryogenic Instrumentation of the DFX
10 temperature transducers (TT):
  Two in vacuum attached to He tank (Cernox): mutual spares
  4 in the splice box (He tank) (Cernox)
  4 temperature sensors attached to the resistive heaters
4 resistive heaters and 1 heat exchanger:
  1 GHe/LHe heat exchanger
  2 resistive heaters in external bath (includes 1 spare)
  2 resistive heater in the lower bath
2 pressure gauges:
  1 He pressure gauge located on the helium gas return line in the QXL
  1 ΔP gauge to measure level of liquid in the fountain
2 LHe level transducers
Cryo valves: part of cryo jumper
Splice box (MgB2/Nb-Ti)

## Slide 11: Cryogenic Instrumentation of the DFX
Temperature transducer wiring:
  4 wires per probe
  2 probes in vacuum  8 wires at vacuum feedthrough:
    >1 m long wires, no thermalization required
    Manganin wires, AWG 36 1
  8 probes in LHe  32 wires at DFX cold mass instrumentation feedthrough:
    Cu wires, AWG 32 1
LHe level transducer:
  2 probes (wires part of the probe)
    Easily replaceable for unscheduled repair work interventions (by design of DFX)
Electrical heater wiring:
  2 wires per heater  8 wires (Cu, cross-sectional area to be confirmed)
1 LHC-Q-GN-0009, EDMS 320597

## Slide 12: Feedthroughs for DFX Voltage Taps and Cryogenic Instrumentation (1)
Two types of feedthrough for instrumentation installed in DFX cold mass:
  Voltage taps (at least two units)
    Must meet insulation voltage requirements, to ground and between circuits, during acceptance tests of components, insulation tests of the system and operation
    Instrumentation wires grouped by circuit, considering voltage ratings
  Temperature probes and resistance heaters (one unit)
Feedthrough based on the concept of the Instrumentation Feedthrough System (IFS) of LHC cryo magnets
  IFS constructed as components tested on the surface and then assembled in the DFX

## Slide 13: Feedthroughs for DFX Voltage Taps and Cryogenic Instrumentation (2)
Cold mass instrumentation wiring (voltage taps, temperature, heater) connected to IFS wiring in a Wiring Interconnection Box (WIB)
WIB located next to Nb-Ti/Nb-Ti splice box to allow access for repairs
Design and procurement of IFS performed by CERN
IFS to provide spare capacity of at least 5%
Wiring Interconnection Box
WIB
Instrumentation Feedthrough System
IFS
Nb-Ti/Nb-Ti Splice Box

## Slide 14: Vacuum Instrumentation of the DFX
The cold powering chain of the inner triplet comprises three vacuum volumes 1:
  DFX, DSH and DFH
The DFX vacuum vessel will be equipped with ports to connect pumping units and vacuum instrumentation 2
All the vacuum instrumentation (Pirani, Penning and membrane gauge) will be external to the DFX vacuum vessel  no wiring is required in the vessel for vacuum instrumentation
1 G. Riddone et al., EDMS 1824906; Y. Leclercq, EDMS 2019348
2 Y. Leclercq, DFX Interfaces, EDMS 2157597

## Slide 15: Summary
Instrumentation in the DFX:
  Protection:
    Electrical protection requirements implemented using ~200 voltage taps over the 19 circuit branches for monitoring and protection
  Cryogenics:
    8 temperature probes, + 2 in vacuum *
    2 level gauges *,
    2 pressure gauges,
    1 GHe/LHe heat exchanger,
    4 resistive heaters
  Vacuum: no vacuum instrumentation routed in the vessel
Instrumentation wires routed to room temperature via Instrumentation Feedthrough Systems (IFS) on the DFX (except those marked * above)

## Slide 16: Extra Slides

## Slide 17: Enlargement of Voltage Tap Configuration

## Slide 18: DFX Instrumentation Layout Proposal
Sketch from Y. Leclercq