## Slide 1: DFM Functional specification
Y. Leclercq on behalf on WP6a DFM team development
CDR DFM 21 June 2019

## Slide 2: Context : DF boxes key functions
DF design
Installation
Integration
Insulation Vacuum
SCLink
Test
Transport
CL / Magnet
Cryogenics
Maintenance
DF system interfaces
D1
CP
Q3
Q2b
Q2a
Q1
IP
Power converters
DSHx
DFHx1
DFX
DFHx2
D2
≈45m
DFHM
DFM
DSHm
≈80m
≈50m
≈8m
Service tunnel
Transverse tunnel
LHC tunnel
Each IP1 and IP5 sides equipped with 2 cold powering chains of cryostats
  Matching sections : DFHm – SC Link - DFM
DFM basic functions:
  Electrical interface between SC Link and superconducting magnets
  Supply cryogenics to the SCLink
DFM functional specification and interface definition EDMS 2052614
1. Basic concept

## Slide 3: General requirements
DFM installed in LHC machine
   Comply with CERN rules
      CERN Safety Rules
      GSI-M-4 - Cryogenic equipment :
   European directives
      Pressure Equipment Directive 2014-68-EU
   HL-LHC QA requirements
      ALARA principle
      Material requirements
      Documentation & MTF
GSI-M4: “The manufacture […] by collaborating institutions, of all new cryogenic equipment shall comply with the applicable CERN Safety Rules, European directives and harmonised standards”.
HL-LHC documentation requirements
Details in spare slide

## Slide 4: Electrical main specifications
DFM shall ensure the electrical connectivity between the SCLink DSHM and D2 cables
SCLink cables layout:
  10 MgB2 conductors in SCLink
  NbTi extensions soldered to MgB2 in protective rigid cylinder
  Only NbTi extensions are accessible in DFM
Magnet cables layout: 10 NbTi conductors from magnet side
The NbTi extensions shall be routed and connected to the NbTi bus coming out of from the plug
Instrumentation shall be routed to feedthroughs on a dedicated patch panel at the level of the vacuum vessel interface (no cold feedthroughs)
SCLink
DFM
Magnet
Side
Plug
NbTi bus from Plug
Rigid protection of MgB2-NbTi splices
NbTi bus from SCLink
Splice
MgB2 cables

## Slide 5: Mechanical interfaces
SCLink Vacuum Jacket flange
Bolted to DFM vacuum vessel
SCLink Helium Jacket flange
Welded to DFM He vessel
MgB2-NbTi
rigid protection
Ø 200
600
NbTi
bus bars
Ø 150
SCLink
DFX
Magnet
Plug
MgB2-NbTi splices
SCLink mechanical interface
  Two independent flexible when installed
  Vacuum & helium jacket flanges fixed to DFM
  MgB2-NbTi splices contained in rigid protection fixed to He jacket flange
  Only NbTi extensions access the DFM He volume
Magnet mechanical interface
  Plug fixed to ground
  DFM fixed to He/vacuum interfaces with bellows
  Access to NbTi-NbTi splices granted during installation and maintenance
Cables thermal contractions
  NbTi-NbTi splices fixed to DFM He vessel
  DFM covers internal contractions 3.5 mm/m
3.5 mm/m
NbTi-NbTi splices
fixed to He vessel

## Slide 6: Cryogenics requirements
Dedicated presentations on Cryogenic scheme, operation, safety
Layout:
Hydraulic plug separates triplet magnet & DFX-SCLink He volumes
Dedicated DFX jumper
Electrical performance:
NbTi cables & MgB2-NbTi splices immersed in LHe
Cryogenic lines:
LHe in, Ghe out, Outlet Magnet line, heat exchanger
Operation configuration
Heaters (electrical & heat exchanger) vaporises helium
  Nominal : 2 g.s-1 , design 3 g.s-1
Ghe gaseous mass flow through the SCLink
Design Pressure : 2.5 bara
Instrumentation:
Level gauges, Temperature sensors, Pressure gauge
Design requirements:
Heat loads to LHe < 20 W
No condensation on external surfaces and feedthroughs
> 10 min of nominal supply GHE in case of liquid supply stop
Constant slope between coldest point and LHE-GHE interface
Safety relief devices to protect DFM+SCLink
Access to safety relief devices, instrumentation interfaces shall be granted for inspection and maintenance
SCLink
DFM
Magnet side
Plug
MgB2-NbTi splices
CS : LHe In
SD : GHe Out
(for transient)
Heat exchanger 40K
E’HFH2
100 W
2 g.s-1
DFM nominal configuration
PT
5 min margin
Superfluid @ 1.9K
Liquid He @ 4.5 K
Gaseous He
Heater
MgB2
NbTi
Splice

## Slide 7: Insulation vacuum
The DFM insulation vacuum shall be compatible with the General WP6a insulation vacuum layout EDMS 2048016
The DFM insulation vacuum is independent to:
  Allow local maintenance & leak detection
  Minimise inter-dependence between helium volumes
 DFM presents vacuum barriers with:
  The cryolines (not part of DFM)
  The SCLink (part of the DFM)
  The Connection to the D2 cryostat (not part of DFM)
Interfaces:
  Standard type flanges with elastomer seal
  Ports for pumps and instrumentation for both DFM & SCLink
  Pressure relief plate
SCLink
DFM
Magnet
Plug
Unit | Value
Insulation vacuum pressure level at ambient temperature | < 1.10-4 mbar
Insulation vacuum pressure level in nominal operation | < 1.10-5 mbar
Maximum allowed overall leak rate in nominal operation | < 2.10-8 mbar.l.s-1
PT
SCLink :
Pumping, gauge, safety port

## Slide 8: Integration specification
DFM
DSHm
D2
CC
CC
≈45 m
≈1.5 m
D2
On-going study to define Integration specifications
Weekly meeting started under WP15 (Friday 10am) to define inputs leading to integration study.
1st Meeting on June 14.
Preliminary studies led with DFX environment (see next talk)

## Slide 9: Preventive maintenance and repairs
Dose up to 1 MGy over HL-LHC life time at D2 end, Neutron f. ≈ > 1.1015 cm-2, up to 25 mSv/h
All operations shall be designed from the ALARA point of view:
  Minimise intervention time (access, automatic operation)
Interventions
  Unscheduled interventions for inspections and light work during Technical Stops (e.g. for electrical checks on patch panel)
  Planned interventions for routine maintenance requiring warm up during YETS (e.g. replacement of burst disks)
  Unscheduled medium repair work interventions requiring warm up during YETS (e.g. Nb-Ti/Nb-Ti repair)
  Unscheduled heavy repair work interventions requiring warm up during EYETS or unscheduled extended machine stop (e.g. MgB2/Nb-Ti repair, plug replacement)
DFM Area
Annual HL-LHC TID at various location for illustration only.
Courtesy G.Lerner
DFX Area

## Slide 10: Manufacturing & Inspections
Manufacturing & Inspections according to
  Pressure Equipment Directive (PED)
  HL-LHC QA requirements (see spec)
    Materials & Manufacturing specific requirements:
      Compatible with Dose level over HL-LHC project period:
      Cobalt content for stainless steel < 0.1%
      Polymers according to IS41 EDMS335806
      Vacuum vessel as PED CATI
      Bellows specific welding interfaces
    Inspections and certifications
      Welding and welders
      Leak tightness level, procedure and operators
      Pressure testing according to PED
    Documentation
      Manufacturing procedures & qualifications
      Inspection reports
      CE certification
      Upload into CERN database MTF
CERN database MTF for manufactured products

## Slide 11: Summary
Cryogenics, Electrical, insulation vacuum operating functional specifications are defined
Integration and transport specifications still to be defined. Specific weekly meeting in place under WP15.
Detailed technical and interfaces specifications to be studied (cryogenics connection, Electrical protection)