## Slide 1: FRAS Motorized Axes Control System
P. PERONNARD
Review of HL-LHC Alignment and Internal Metrology (WP15.4)

## Slide 2: Outline
The control system requirements
Solution proposed: SAMbuCa
Development Timeline
Conclusions

## Slide 3: FRAS Motorized axes IP5 summary
Racks location | Racks names | Cable length up to the sensors / actuators (m) | Axes type | Axes number | Axes` groups to be synchronized
UL557 | GYPOS_01 ÷ GYPOS_04 | 100 | Motion (stepping motor + resolver) | 60 | 30 +30
 |  |  | Load cells(TBC) | 36 ÷ 60 | 0
 |  |  | Position sensors (TBC) | 60 | 0
UR55 | GYPOS_01_R ÷ GYPOS_06_R | 300 | Motion (stepping motor + resolver) | 71 | 24+16+10+10+10
 |  |  | Load cells(TBC) | 31 | 0
 |  |  | Position sensors (TBC) | 31 | 0
UR55 | GYPOS_01_L ÷ GYPOS_06_L | 300 | Motion (stepping motor + resolver) | 71 | 24+16+10+10+10
 |  |  | Load cells(TBC) | 31 | 0
 |  |  | Position sensors (TBC) | 31 | 0

## Slide 4: FRAS Motorized axes IP1 summary
Racks location | Racks names | Cable length up to the sensors / actuators (m) | Axes type | Axes number | Axes` groups to be synchronized
UR15 | GYPOS_01 ÷ GYPOS_04 | 100 | Motion (stepping motor + resolver) | 60 | 30 +30
 |  |  | Load cells(TBC) | 36 ÷ 60 | 0
 |  |  | Position sensors (TBC) | 60 | 0
US15 | GYPOS_01_R ÷ GYPOS_06_R | 300 | Motion (stepping motor + resolver) | 71 | 24+16+10+10+10
 |  |  | Load cells(TBC) | 31 | 0
 |  |  | Position sensors (TBC) | 31 | 0
US15 | GYPOS_01_L ÷ GYPOS_06_L | 300 | Motion (stepping motor + resolver) | 71 | 24+16+10+10+10
 |  |  | Load cells(TBC) | 31 | 0
 |  |  | Position sensors (TBC) | 31 | 0

## Slide 5: FRAS Motorized axes summary
Axes type | Total Axes number
Motion (stepping motor + resolver) | 400
Load cells (TBC) | 194 ÷ 244
Position sensors (TBC) | 244
Limits switches | 1044

## Slide 6: Control System Requirements
Sensors / Actuators | 
Sensors / Actuators Total Integrated Dose (TID) | < 2 MGray
Sensors / Actuators cable length from the electronics | 300 m
Maintenance | free
Life time | Min 10 years
Operation time | 86 h

## Slide 7: Control System Requirements
Control system architecture & components | 
Axes positioning resolution | few µm
Axes motion synchronization | 1s per axes` groups (system can achieve 1 ms)
Motion start trigger | Software trigger
Modularity | Architecture scalable with number and axes` groups position in the racks
Flexibility | Conditioning electronics proper designed for the project actuators / sensors
Fields I/O connectivity | High Density / High robustness to avoid false contacts and oxidation
Maintainability | Mean Time To Repair < 10min
Long term investment | Full control of hw and sw for future upgrades / improvements

## Slide 8: Control system architecture

## Slide 9: Low-level control: SAMbuCa (Sensors Acquisition & Motion Control system)
Complete In-house solution (i.e. hw and sw)
Architecture :
  PXIe Front-ends in High Availability chassis
  a PXIe FPGA Carrier and a set of FMC cards to cover the interfacing requirements with the field sensors and actuators
  EN-SMM step driver (long cables, open/closed loop)
  Focus on connection reliability and re-configurability
  PXIe chosen as successor of the PXI standard that is getting obsolete - Platform fully standardized at CERN with BE-CO (i.e. Cent OS 7 and C++)
  Same control system solution to be adopted for the LHC Collimators low level control upgrade (HL-LHC – Collimation System International Review Feb2019)

## Slide 10: Low-level control: SAMbuCa (Sensors Acquisition & Motion Control system)
PXIe Controller
  Based on COM-Express CPU modules
  Computing power chosen according to user needs
Will run Be/CO Linux and FESA class
Software framework and Linux drivers to configure and control the peripheral cards
Collaboration with BE/CO to ensure the compatibility with their ecosystem– Open Hardware
Design in progress – Outsourced to external company

## Slide 11: Low-level control: SAMbuCa (Sensors Acquisition & Motion Control system)
PXIe FMC Carrier
  Based on Xilinx Zynq UltrasScale+
  PCIe Gen2x4
  4GB DDR4 memory with ECC for processor
  2GB DDR4 memory for programmable logic
  64GB eMMC flash
  Remotely reconfigurable from PXIe controller
  White-Rabbit support for synchronization
  HPC FMC connector fully wired to FPGA
  Board layout in progress, prototype expected by Q4 2019
Control algorithms executed either by ARM cores or programmable logic

## Slide 12: Low-level control: SAMbuCa (Sensors Acquisition & Motion Control system)
Set of FMC cards
  8-ch LVDT/Resolver/Potentiometer analog front-end
  12-ch Thermocouple/PT100
  Digital IOs (limit switch, interlock, motor driver, …)
  Strain gauge
  Force sensor
  Optical fiber card to connect an expansion chassis (CompactPCI serial from BE/CO)

## Slide 13: Low-level control: SAMbuCa (Sensors Acquisition & Motion Control system)
Expansion chassis with DIOT (WP18 HL-LHC)
  https://wikis.cern.ch/display/DIOT/Distributed+IO+Tier+chassis
  Possibility to connect up to 4x chassis to PXIe FMC carrier
  Can be an option for slow application

## Slide 14: Low-level control: SAMbuCa (Sensors Acquisition & Motion Control system)
Rack layout example
  4 expansion chassis connected to PXIe FMC carrier via optical links
Expansion Chassis #1
PXIe Chassis (8 peripheral slots)
PXIe Controller
Application FMC Card
Expansion System Controller with FMC carrier
PXIe Survey & Motion FMC carrier
Expansion Chassis #2
Expansion Chassis #3
Expansion Chassis #4

## Slide 15: Development Timeline
Proof of concept 2020
FRAS control system validation on string tests
Mass production and validation 2022-2023
Operational software 2024
Deployment and commissioning 2025-2026

## Slide 16: Conclusions
Design study shared with LHC collimator control system
Building blocks profit of BE/CO developments foreseen in WP18 HL-LHC (expansion chassis)
SAMBUCA will ensure with respect to commercial solutions
  Full control on hardware and software components
  High-availability ensured by 15-years past experience on motion control for critical missions (e.g. LHC collimator control system)

## Slide 17: Thank you