## Slide 1: WP17.2 – Electrical distribution Power distribution LS3 De-cabling works phasing and durations in LSS1-5
N. Dos Santos on behalf of HL-LHC_EN-EL team (for electrical distribution)
EDMS: 2258944

## Slide 2: Summary
Works baseline
EN-EL electrical distribution
  Services and cables to remain LIVE during CE cores works
  LSS1 services displacement
  LSS5 services displacement
LS3 works breakdown, durations and costs estimation status (electrical distribution only)
Conslusions/Next steps
Reminder of
presentation done end-Jun 19
EDMS 2258938
Reminder of
presentation done end-Jan 18
EDMS 1896611

## Slide 3
Reminder of
presentation done end-Jan 18
EDMS 1896611

## Slide 4: Context and requests
Areas Sectorisation
  LHC 1 :
    Secteur 1 : Zone interne USA15 (sans tunnel),
    Secteur 2 : Zone interne US15 (sans tunnel)
    Secteur 3 : Zone tunnel (RR13 jusqu’à l’UX15) en prenant tout ce qui est interne au tunnel et ce qui va vers les zones de services
    Secteur 4 : Zone tunnel (l’UX15 jusqu’au RR17) en prenant tout ce qui est interne au tunnel et ce qui va vers les zones de services
  LHC 5 :
    Secteur 1 : Zone interne USC55 (sans tunnel)
    Secteur 2 : Zone interne UL55-UJ56 (sans tunnel)
    Secteur 3 : Zone tunnel (RR53 jusqu’à l’UXC55) en prenant tout ce qui est interne au tunnel et ce qui va vers les zones de services
    Secteur 4 : Zone tunnel (UXC55 jusqu’au RR57) en prenant tout ce qui est interne au tunnel et ce qui va vers les zones de services
Hypothesis and boundary conditions
  For the LHC machine we take the hypothesis that all cables going from technical caverns to equipment between Q6 and Q6 must be dismounted + services areas concerned by LHC
  For the other cable systems we take the hypothesis to dismount all cables and equipment inside LHC new cores areas (UAs and ULs cores)
Cost estimation granularity
  Cables “LHC Machine” to be permanently dismounted
  Cables “Security Systems” serving the HL-HLC area that has to be temporarily removed
  Cables “Service Generaux” serving the HL-HLC area that has to be temporarily removed
  Cables (machine and other) not link to HL-LHC but “crossing the areas” and so also eventually affected by HL-LHC so that have to be temporarily removed
Reminder of
presentation done end-Jan 18
EDMS 1896611

## Slide 5: Assumptions for the Cost Estimation
Only cables in EL cables DataBase
  Not documented cables are not counted in EL estimations – for ex.:
    Cables pulled by experiments
    Cables between EL distrib. and monorail
    …
Only equipment belonging to EL
  Not counted in EL estimations – for ex.:
    Signal boxes installed by EL but belonging to others
    Power sockets strips installed by others
    …
Only fibre optics installed by EL
  Not counted in EL estimation users or experience fibres
Assumptions:
  Prices based on actual EL installation contracts: S213 (cabling) – S214 (FO) (prices from 2016)
  Straight dismounting approach – 1 phase per point
  Rate exchange: 1 EUR = 1.2 CHF
  Costs Uncertainty: Rank 3-4 according -10%, +20%
Extra costs not considered in EL cost estimation:
  M4P for preparation and execution phases – different budget according HL-LHC C&R
  Safety compensatory measures during de-installation EL work phase and next
  Civil eng. and metallic structures modifications required for EL equipment
  Handling and transport of equips and cables
  Treatment of irradiated cables and equipment
  Personnel radiation protections for radiation areas during de-installation work
  Others cables and equips not documented in EL DB
Reminder of
presentation done end-Jan 18
EDMS 1896611

## Slide 6: Assumptions for the Cost Estimation
Each LHC points divided in 4 sectors:
  2 services sectors and 2 tunnel sectors
  Each sector was sub-divided on 2 main de-installation activities for:
    LHC machine definitive de-installation (Q6-Q6, UL55, USC55, UL14-16, US15
    New cores creation LHC tunnel (UAs and ULs)
Cables and equipment related to LHC machine definitive de-installation :
  Removal of all EL existing equipment related to LHC machine, ex.:
    Power socket boxes +distribution boxes dedicated to Vacuum systems in tunnel
  Removal of all cables connecting to LHC machine equipment (inside LHC tunnel and services areas)
4 Sectors identified in LHC 5
Reminder of
presentation done end-Jan 18
EDMS 1896611

## Slide 7: Assumptions for the Cost Estimation
Cables and equipment related to new cores creation inside LHC tunnel (UAs and ULs)
  Removal of all EL existing equipment inside of the tunnel near CE works for new cores drilling areas +10 m from each side of the cores. Equip. ex.:
    Pw socket boxes and platines, luminaires, “tableautins”, cable trays & supports, “goulotte sécurité”
De-installation of all cables (pw and signal) & fibres identified by EL in transit inside CE work areas – whole length of the cables between source connection point, ex.: cable from SE1 to RR13
Reminder of
presentation done end-Jan 18
EDMS 1896611

## Slide 8
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 9: EN-EL electrical services
Services maintained and to be keep LIVE during cores drilling works:
  Arrêt d’Urgence Généraux (AUG) – AUG buttons installed on “tableautins”
  Lighting:
    Switched (normal lighting commanded by CCC)
    Permanent (minimum lighting)
    Safety (luminaires installed on «tableautins»)
  General power distribution sockets (F1) – blue distribution boxes
  Main 18 kV power distribution loop – present in the «caniveau»
Cables locked-out but to keep if possible
  18 kV cable dedicated to RRs power converters
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 10: LSS1L – RI13
New temporary power cabling for lighting and F1 distribution boxes
UPR cables
& ladder
LHC Power cables & ladders
Switched and permanent luminaires
Power distribution coffrets – F1, F2 and F3 & plugs
Tableautins
Tableautins
Power cables & ladders
Power sockets for Vacuum
Power sockets for Vacuum
UA Cores area
UL Cores area
UPR cables
& ladder
New temporary power cabling for lighting and F1 distribution boxes
Displacement of 18 kV cable and EL safety cables
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 11: LSS1R – RI17
Same proposition as for LSS1L – RI13
(see previous slide)
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 12: LSS1R – RI13 & RI17 - Tableautins
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 13: LSS5L – R53 & R54
Tableautins
Power sockets for Vacuum
UA Cores area
UL Cores area
New temporary power cabling for lighting and F1 distribution boxes
Displacement of 18 kV cable
Displacement of safety power cables (goulotte s.)
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 14: LSS5R – UJ57
UL Cores area
Non modified safety power cables location (goulotte sécurité)
Futur UL cores
CE red area to be modiffied (proposition)
Modified safety power cables location (goulotte sécurité), to be checked again on site /!\
Dismatling of 18 kV cable (power convereters)
CE agreed on this proposition?
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 15: LSS5R – UJ57
Displacement of few safety power cables (cables to be checked)
New temporary power cabling for lighting and F1 distribution boxes
Mechanical protection
Dismatling of 18 kV cable (power convereters)
UPRs cables & ladder
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 16: LSS5R – R57
New temporary power cabling for lighting and F1 distribution boxes
Mechanical protection
Dismatling of 18 kV cable (power convereters)
UPRs cables & ladder
UPRs cables & ladder
No displacing of Safety power cables (goulotte s.)
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 17: LSS5 – R53/54 & UJ57/R57 - Tableautins
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 18: Conclusions/Next steps
UJ57 displacement of safety cables to be investigated more in detail (EL or users cables)
UJ57 CE exclusion (red) area to be redefined
Mechanical protection of the remaining LIVE services to be defined by CE, in collaboration with EL
State about the EL safety systems needed inside CE exclusion (red) areas
CE works planning during LS3?
Cores diameters possible reduction?
Tb done by EL
?
Tb done
CE will assure safety of their personnel
Discussions on-going
Reminder of
presentation done end-Jun 19
EDMS 2258938

## Slide 19
LS3 Works breakdown for dismantling and re-installation of LSS1 & LSS5

## Slide 20: WP15 - LS3 Planning for C&SR Nov 2019
EDMS 2254475
For comments
(see next slides)

## Slide 21: WP15 - LS3 Planning for C&SR Nov 2019
New baseline w/r to Jan 2018 presentation/baseline:
  All machine “coffrets” to be removed from D1 to Q6
  Keep and displace safety cables and some 18 kV cables
  Install temporary cables & connection for F1 power lines and lighting
  Temporary cable tray for LSS5R (tbc)
  Design on-going: new cable trays modifications according new machine layout  also impacts general services & machine cabling
Assumptions for next 2 slides (phasing & durations):
  Each of next 2 slides refers only to LSS1L & LSS5R (LSS1L~LSS1R & LSS5R~LSS5L)
  Only 1 shift of 8h/day
  Works not considered at this stage: new machine layout design
  EL works impact:
    Local work  co-activities possible
    No co-activities with others  only EL workers, mainly for cabling pulling

## Slide 22: LS3 Electrical distribution works phasing and durations LSS 1L (only)
To be defined once requests known

## Slide 23: LS3 Electrical distribution works phasing and durations LSS 5R (only)
To be defined once requests known

## Slide 24: Conclusions/Next steps
Validate proposed works phasing  WP15-EL(ENP-FC)
Services & cables displacement propositions during cores works to be approved
Safety constraints in LHC sectors during works (cores & cabling & machine installation) to be defined
New LHC tunnel layout on-going  impact on dismantling/re-installation of pw cabling, cable trays, lights & power boxes  impact on schedule durations & costs
New machine power requests in LHC tunnel  to be announced/requested by concerned WPs

## Slide 25: Conclusions/Next steps
Costs estimations (for power distrib.):
  For dismantling: to be re-evaluated as baseline changed for equipment removal and temporary repowering  WP15 budget
  For re-installation
    General services: not estimated  WP15 budget
    Machine “coffrets”: no requests  WPs requestor budget
  Deadlines?
Manpower for power distrib. under discussion

## Slide 27
Backup slides

## Slide 28: LSS1L – RI13 Cores impact forecast
Courtesy S. Maridor (presentation in 2018)

## Slide 29: LSS1L – RI13 Cores impact forecast

## Slide 30: LSS1L – RI13 Cores impact forecast
Courtesy S. Maridor (presentation in 2018)

## Slide 31: LSS5R – UJ57
Courtesy S. Maridor (presentation in 2018)

## Slide 32: RESUME

## Slide 33
LHC
RR53
R532

## Slide 34
HL-LHC
RR53
R532

## Slide 35
LHC
R532

## Slide 36
HL-LHC
R532

## Slide 37
LHC
R532

## Slide 38
HL-LHC
R532

## Slide 39
LHC
UJ53

## Slide 40
HL-LHC
UJ53
ZONE DFM - A MODIFIER

## Slide 41
LHC
R541
RZ54

## Slide 42
HL-LHC
R541
RZ54