## Slide 1: SIRIUS converter family
CERN-TE-EPC 13 June 2017

## Slide 2: Overview
Introduction to Sirius Family
  Target applications
  Choosing the right model
Design industrialisation
  Production file
  Testing aids
ALBA pre-study
  Bending magnets
  Quadrupole magnets
  Budget allocation

## Slide 3: Introduction to Sirius
Magnet type | Total (1.2sec) | Recoverable | Thermal loss (1.2sec)
Quadrupole (26Gev) | 11kJ | 6kJ | 5kJ
Small Dipole (26Gev) | 31.5kJ | 25kJ | 6.5kJ
Large Dipole (26Gev) | 101kJ | 82kJ | 19kJ
* Assuming cost of electricity of 0.045 CHF/kWh. 1kJ of energy over a 1.2sec cycle corresponds to 1kJ/1.2sec=0.83kW of average power. Assuming this 1.2sec (PS) cycle repeats for 24hours over 270 working days the total energy required from the power network (for each 1kJ) is 5378kWh/annum. If this energy is not recovered in capacitor banks after every magnet cycle it is returned to the power network and is not remunerated by the provider.
Annual cost of electricity of each 1kJ of losses:
(Non-recoverable/consumed every 1.2seconds)
242 CHF*
Sirius is primarily suitable for:
Cycling applications with considerable amounts of recoverable energy
RMS loss minimisation and magnet field conditioning (with FGC3)
Long life and fast cycling

## Slide 4: Power Converter for Transfer lines
Standardised converter brick
SIRIUS S
SIRIUS S 30kJ
SIRIUS 2P 60kJ
SIRIUS 2P 120kJ
SIRIUS 2P 180kJ
SIRIUS 2P
SIRIUS 4P
SIRIUS S 60kJ
SIRIUS S 90kJ
SIRIUS 4P 120kJ
SIRIUS 4P 240kJ
SIRIUS 4P 360kJ
Extra cabinet for energy storage: SIRIUS 4P+ 600kJ
Energy recovery bank 30-90kJ

## Slide 5: Power Converter for Transfer lines
SIRIUS S
SIRIUS S 30kJ
SIRIUS 2P 60kJ
SIRIUS 2P 120kJ
SIRIUS 2P 180kJ
SIRIUS 2P
SIRIUS 4P
SIRIUS S 60kJ
SIRIUS S 90kJ
SIRIUS 4P 120kJ
SIRIUS 4P 240kJ
SIRIUS 4P 360kJ
Extra cabinet for energy storage: SIRIUS 4P+ 600kJ

## Slide 6: Power Converter for Transfer Lines
200kJ
113kJ
900V
450V
450A
900A
1800A
SIRIUS 2S
Imagnet,rms: 200A
Pmagnet,rms: 30kW
Emagnet,max: 56kJ
SIRIUS S
Imagnet,rms: 200A
Pmagnet,rms: 15kW
Emagnet,max: 28kJ
SIRIUS 2P
Imagnet,rms: 400A
Pmagnet,rms: 30kW
Emagnet,max: 56kJ
SIRIUS 4P
Imagnet,rms: 800A
Pmagnet,rms: 60kW
Emagnet,max: 113kJ
SIRIUS 4P*
Imagnet,rms: 800A
Pmagnet,rms: 60kW
Emagnet,max: 200kJ
Imagnet,peak
Vmagnet,peak
56kJ
28kJ
56kJ
113kJ
SIRIUS 2P2S
Imagnet,rms: 400A
Pmagnet,rms: 60kW
Emagnet,max: 113kJ
NOTE! Sirius a Fast Pulsed converter range exists too!

## Slide 7: Choosing the right model
Output power limited by the front-end Boost stage power rating
Recoverable magnet energy is limited by the built-in capacitive storage1 (0 to 7 banks per power brick2)
15kW
Output RMS current is limited by the output H-bridge stage ratings and lifetime3 considerations
30kW
60kW
200A
400A
800A
Complete specification: http://section-mpc.web.cern.ch/content/converters/sirius/general
77kJ
144kJ
288kJ
3 assuming 200million cycles with 1.2second period
Sirius S
Sirius 2P
Sirius 4P
450A peak
1800A peak
900A peak
2 capacitor banks 4 to 7 require additional rack
1 moderate dc-link discharge depth of 300V

## Slide 8: Choosing the right model
Selection curves:https://edms.cern.ch/document/1540790/1
Not
OK
OK
Voltage ratings not enough
High RMS losses
Energy storage limited

## Slide 9: Design Industrialisation

## Slide 10: Design industrialisation
The main principles:
  Standardise solution across different projects
    Produce in large scale -> lower prices
  Create a complete production file
    No development effort for supplier -> wide range of bidders
  Cern supply of critical components (to maintain the know-how)
    DCCTs, power stacks where made by specialist companies -> reduce risks
  Use off-the-shelf parts where possible
    Energy storing capacitors
    Metal cabinets
    All switchgear
Test tools made for industry and troubleshooting

## Slide 11: Production file
Production file contents:
Electronic Schematics (1 per model)
Mechanical drawings (~130 drawings)
Bill of materials (electromechanical)
List of cables
Suppliers list (suggestions)
Items specified/tendered for by CERN:
magnetic materials
power stack
DCCT
RegFGC3 chassis and cards

## Slide 12: The ALBA pre-study

## Slide 13: User requirements

## Slide 14: Bending magnets
Quantity | Value |  | Unit | notes
APPLICATION DERIVED PARAMETERS |  |  |  | 
LMAGNET | 0.1 | 0.1 | H | 
RMAGNET | 0.355 | 0.355 | 0.355 | Includes 20mOhm cabling
IMAGNET,sat | ? | ? | A | 
Imin | 20 | 20 | A | 
Imax | 700 | 700 | A | Converter rating: 900A
Vmax | 500 | 500 | V | Converter rating :900V
Energy to recover | 25 | 25 | kJ | 1 cap bank per brick
Rise time (Tr) | 0.19 | 0.19 | Sec | 
Fall time (Tf) | 0.11 | 0.11 | Sec | 
Flat-top duration (Tft) | 0.01 | 0.01 | Sec | 
Period time | 0.32 | 0.32 | Sec | 
Current RMS 4s | 410 | 410 | A | See note 1
Current RMS 40s | 39 | 39 | A | 
Current DC max | 400 | 400 | A | See note 2
Power Peak | 350 | 350 | kW | 
Power 4s | 59.7 | 59.7 | kW | Converter rating: 60kW
Operating time | 5700 | 5700 | h/annum | 
Cycles | 17100 | 17100 | Cyc/annum | See note 3
Cycles in lifetime | 342000 | 342000 | Cycles | In 20 years
CONVERTER PARAMETERS |  |  |  | 
Solution | 2x SIRIUS 2P2S Input: 3ph, 400V, 125A, cosφ:0.93, THD:30% Output: 900VPK,900APK, 400ARMS, 60kWRMS, ERecoverable:132kJ) |  |  | 
Simplified (trapezoid) cycle
Fast ramping with 500V

## Slide 15: Bending magnets
Sinusoidal cycle
Irms=459A
P=74.8kW (over 0.320s)
Semi-sinusoidal cycle
Irms =282A
P=52.6kW (over 0.320s)
Extraction instance

## Slide 16: Booster Quadrupole magnets
Quantity | Value |  | Unit |  | notes | 
APPLICATION DERIVED PARAMETERS |  |  |  |  |  | 
LMAGNET | 0.0272 | 0.0272 | H | H | 8 magnets in series | 8 magnets in series
RMAGNET | 0.44 | 0.44 | Ohm | Ohm | *discrepancy with spec | *discrepancy with spec
IMAGNET,sat | ? | ? | A | A |  | 
Imin | 0 | 0 | A | A |  | 
Imax | 180 | 180 | A | A | Converter rating: 450A | Converter rating: 450A
Vmax | 81 | 81 | V | V | Converter rating: 450V | Converter rating: 450V
Energy to recover | 0.4 | 0.4 | kJ | kJ |  | 
Rise time (Tr) | 0.24 | 0.24 | Sec | Sec |  | 
Fall time (Tf) | 0.04 | 0.04 | Sec | Sec |  | 
Flat-top duration (Tft) | 0.01 | 0.01 | Sec | Sec |  | 
Period time | 0.32 | 0.32 | Sec | Sec |  | 
Current RMS 4s | 102 | 102 | A | A | Converter rating: 200A | Converter rating: 200A
Current RMS 40s | 10 | 10 | A | A |  | 
Current DC max | 185 | 185 | A | A | Converter rating: 200A | Converter rating: 200A
Power Peak | 14.6 | 14.6 | kW | kW |  | 
Power 4s | 4.6 | 4.6 | kW | kW |  | 
Operating time | 5700 | 5700 | H | H |  | 
Cycles | 17100 | 17100 | Cycles/annum | Cycles/annum |  | 
Cycles in lifetime | 342000 | 342000 | Cycles | Cycles | In 20 years | In 20 years
CONVERTER PARAMETERS |  |  |  |  |  | 
Solution | SIRIUS S Input: 3ph, 400V, 32A, cosφ:0.93, THD:30% Output: 450VPK,450APK, 200ARMS, 15kWRMS, ERecoverable:33kJ) |  |  |  |  | 

## Slide 17: Booster QS340
Quantity | Value | Unit | notes
APPLICATION DERIVED PARAMETERS |  |  | 
LMAGNET | 0.048 | H | 8 magnets in series
RMAGNET | 0.61 | Ohm | *discrepancy with spec
IMAGNET,sat | ? | A | 
Imin | 0 | A | 
Imax | 180 | A | Converter rating: 450A
Vmax | 115 | V | Converter rating: 450V
Energy to recover | 0.8 | kJ | 
Rise time (Tr) | 0.24 | Sec | 
Fall time (Tf) | 0.05 | Sec | 
Flat-top duration (Tft) | 0.01 | Sec | 
Period time | 0.32 | Sec | 
Current RMS 4s | 105 | A | Converter rating: 200A
Current RMS 40s | 10 | A | 
Current DC max | 157 | A | Converter rating: 200A
Power Peak | 20.7 | kW | 
Power 4s | 6.7 | kW | 
Operating time | 5700 | H | 
Cycles | 17100 | Cycles/annum | 
Cycles in lifetime | 342000 | Cycles | In 20 years
CONVERTER PARAMETERS |  |  | 
Solution | SIRIUS S Input: 3ph, 400V, 32A, cosφ:0.93, THD:30% Output: 450VPK,450APK, 200ARMS, 15kWRMS, ERecoverable:33kJ) |  | 

## Slide 18: Booster QC340
Quantity | Value | Unit | notes
APPLICATION DERIVED PARAMETERS |  |  | 
LMAGNET | 0.216 | H | 8 magnets in series
RMAGNET | 2.36 | Ohm | *discrepancy with spec
IMAGNET,sat | ? | A | 
Imin | 0 | A | 
Imax | 180 | A | Converter rating: 450A
Vmax | 460 | V | Converter rating: 450V
Energy to recover | 3.5 | kJ | 
Rise time (Tr) | 0.24 | Sec | 
Fall time (Tf) | 0.06 | Sec | 
Flat-top duration (Tft) | 0.01 | Sec | 
Period time | 0.32 | Sec | 
Current RMS 4s | 105 | A | Converter rating: 200A
Current RMS 40s | 10 | A | -
Current DC max | 113 | A | Converter rating: 200A
Power Peak | 82.8 | kW | 
Power 4s | 25.9 | kW | 
Operating time | 5700 | H | 
Cycles | 17100 | Cycles/annum | 
Cycles in lifetime | 342000 | Cycles | In 20 years
CONVERTER PARAMETERS |  |  | 
Solution | SIRIUS 2S Input: 3ph, 400V, 63A, cosφ:0.93, THD:30% Output: 900VPK,450APK, 200ARMS, 30kWRMS, ERecoverable:66kJ) |  | 

## Slide 19: Budget allocation
The bending circuits are expected to cost approximately 55% of the overall budget.
Chart: Budget Allocation
| Bending | QS180 | QS340 | QC340
 | 6 | 2 | 1 | 1.84

## Slide 20: Annex

## Slide 21: Limited grid power strategy
Energy supply
Energy recovery
Dc-link recharge

## Slide 22: Grid disturbances
Nominal grid
Grid overvoltage
(0.4s – 0.5s)
Grid disconnection
(0.40s – 0.45s)

## Slide 23: Energy storage module
Energy/capacitor
  Theoretical at 400V  2320J
  Actual (tol.-15%) 1972J
  Operating at 300V  1660J
  Usable 300V to 200V 616J
Energy/module (15 caps)
  Theoretical  34800J
  Usable 9243J
Maximum 3 modules per brick
Customisation to increase total energy to 1MJ

## Slide 24: SIRIUS proof-of-concept
Uout
Imagnet
UDCA
UDCB
Iboost
Imagnet
https://edms.cern.ch/document/1506381/1
125kWpk
10kWpk

## Slide 25: The SIRIUS converter