## Slide 1: CMS and ALICE ongoing work report Marcin Ciupinski
16.12.19

## Slide 2: CMS
GasSystem Surface 24VDC current consumption | NOK | sensor not yet connected or cabling to be verified
GasSystem Underground 24VDC current consumption | NOK | sensor not yet connected or cabling to be verified
GasSystem Underground 18VDC current consumption | NOK | sensor not yet connected or cabling to be verified
GasSystem Surface 24VDC current consumption | NOK | sensor not yet connected or cabling to be verified
GasSystem surface Valves DC circuit breaker status | NOK | to be verified why is active
T1 (CSC)
GEM
pump outlet filter differential PT | NOK/OK | sensor not yet connected
Exhaust filter differential pressure transmitter | NOK | sensor not yet connected
CSC
Purifier IOCheck/tests not done as purifier is not connected Exhaust new PDT sensor not yet connected
DT
All purifiers IOCheck done but not yet used after system restart Analysis module still to be fully tested when will be moved from AUX PDT in exhaust not yet connected
RPC

## Slide 3: ALICE
CPV
ALICE CPV Humidifier not yet tested
- IOcheck and logic test to be done
GasSystem Underground 24VDC current consumption | NOK | not connected or cabling to be verified
GasSystem Underground 18VDC current consumption | NOK | not connected or cabling to be verified
HMP
GasSystem Surface 24VDC current consumption | NOK | not connected or cabling to be verified
GasSystem Underground 24VDC current consumption | NOK | not connected or cabling to be verified
GasSystem Underground 18VDC current consumption | NOK | not connected or cabling to be verified
Pump outlet filter differential PT | NOK | sensor not yet connected
TOF
GasSystem Underground 18VDC current consumption | NOK | sensor in IOError - cabling to be check
pump outlet filter differential PT | NOK | sensor not yet connected
Exhaust filter differential pressure transmitter | NOK | sensor not yet connected
Mixer and exhaust pressure regulator | NOK | not yet connected or not working
Distribution rack chamber pressure PT6104 | NOK | sensor not connected
MTR
pump outlet filter differential PT | NOK | sensor not yet connected
Exhaust filter differential pressure transmitter | NOK | sensor not yet connected
Xenon recuperation module |  | logic still to be validated with Louis-Philippe
Pump circuit breakers feedbacks |  | to be check if already connected
Pump temperature sensors | NOK | sensors not connected - to be check if there is a plan to connect it as sensors are in IOError already since at least 2 years
Gas system surface AC circuit breaker LED on but all the CB are ON | NOK | cabling of Digital input to be check
TRD