## Slide 1: CMS-RPC Regulation Valve Test Summary
Sabino Zagaria
EP-DT-FS
21/01/2020

## Slide 2: CMS-RPC Regulation valves
Manual valves in Pre-Distribution Output
Equalize pressure between different detector zones
Detector pressure regulation is done basing on sensors at rack level
→ Weight of hydrostatic column is not taken into account
→ Particularly critical during filling and emptying phase

## Slide 3: New regulation valves
Replacement of manual valves for better and automated regulation
→ LAB Characterization
→ Test in USC

## Slide 4: Valves List
 | VALVE | TYPE/description | FEEDBACK | COST [CHF]
1 | ROTAREX | MANUAL | NO | 100
2 | ROTAREX WITH GULEX MOTOR | ACTUATED MANUAL | YES | 1400
3 | ASCO DN4 | SOLENOID | YES* | 440
4 | ASCO DN15 | SOLENOID | YES* | 320
5 | ASCO DN20 | SOLENOID | YES* | 315
6 | BURKERT 8mm | SOLENOID | NO | 420
7 | BURKERT 9.5mm | SOLENOID | NO | 340
8 | BURKERT 12 | SOLENOID | NO | 780
10 | BURKERT 12S | SOLENOID | NO | 500
11 | RESOLUTIONAIR | PINCH VALVE *(control: PWM+DIGITAL BINARY) | NO | 1300
12 | BRONKHORST F004 | SOLENOID *(control 70-190 mA) | YES | 1460
13 | FESTO | ELECTROPNEUMATIC Pinch valve | NO | 710
14 | FESTO | ELECTROPNEUMATIC Boisseau sphérique asservie par un contrôleur | NO | 620
15 | ECONEX | ELECTRO ACTUATED | NO | 500
16 | VON ROHR | ELECTROPNEUMATIC | YES | 3300
In the market do not exist valves with our requirements
Mostly classic control signal: 4-20mA
Many of them designed for higher pressure applications → difficult regulation in low pressure ranges
Silicon free
Aging test passed

## Slide 5: LAB Test Setup
Flowmeter
Pressure sensor
Tested Valve
Pressure reading
Controller
5
4
3
2
1

## Slide 6: Manual Valve
Currently installed
Used as reference
Chart: Manual valve - N2
| 0 | 0.25 | 0.5 | 0.75 | 1 | 1.25 | 1.5 | 1.75 | 2 | 2.25 | 2.5 | 2.75 | 3 | 3.25 | 3.5 | 3.75 | 4 | 4.25 | 4.5 | 4.75 | 5 | 5.25 | 5.5 | 5.75 | 6 | 6.25 | 6.5 | 6.75 | 7 | 7.25 | 7.5 | 7.75 | 8 | 8.25 | 8.5 | 8.75
16 l/min | 1.9 | 1.9 | 1.9 | 1.9 | 1.95 | 1.9 | 1.95 | 2 | 2 | 2 | 2 | 2 | 1.95 | 2 | 2 | 2 | 2.05 | 2.1 | 2.1 | 2.2 | 2.3 | 2.4 | 2.55 | 2.8 | 3 | 3.2 | 3.5 | 4 | 4.6 | 5.1 | 5.7 | 7.2 | 9.6 | 16.2 | 52.3 | 350
32 l/min | 4.2 | 4.2 | 4.3 | 4.2 | 4.3 | 4.3 | 4.4 | 4.4 | 4.3 | 4.5 | 4.5 | 4.4 | 4.4 | 4.4 | 4.5 | 4.6 | 4.7 | 4.9 | 5 | 5.4 | 5.7 | 6 | 6.6 | 7.3 | 8.4 | 9.3 | 10.3 | 11.9 | 14.3 | 16.2 | 18.5 | 23.9 | 33.8 | 58.8 | 176.5 | 533
Chart: Manual valve - R134a
| 0 | 1 | 2 | 3 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.25 | 8.5 | 8.75
285 l/h | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 5 | 9 | 27 | 290
570 l/h | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 7 | 10 | 17 | 28 | 141 | 658

## Slide 7
Chart: General Comparison – 16 l/min N2
| 100 | 88.6 | 77.099999999999994 | 65.7 | 54.3 | 42.9 | 31.4 | 25.7 | 20 | 14.3 | 8.6 | 2.86 | 0
manual | 1.9 | 2 | 2 | 2 | 2.1 | 2.3 | 3 | 3.5 | 4.6 | 5.7 | 9.5 | 76.2 | 398.8
GULEX MOTOR | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 5 | 7 | 10 | 30 | 68 | 443
Festo sphere | 1 | 1 | 2 | 3 | 4 | 5 | 12 | 48 | 948
Burkert 8 | 2.1 | 2.2 | 2.8 | 3.2 | 3.6 | 3.7 | 3.8 | 3.9 | 4.1 | 4.2 | 4.4 | 4.5 | 4.7 | 5 | 5.3 | 5.6 | 6 | 6.3 | 6.6 | 7 | 7.7 | 8.4 | 9.7 | 11 | 11.5 | 13.2 | 15.4 | 19.3 | 21.5 | 25.4 | 28.8 | 35.4 | 42.6 | 51.8 | 66.7 | 80.7 | 140.8 | 200.5 | 227.8 | 270.4 | 320 | 377
Burkert 9.5 | 1.9 | 2 | 2.2 | 2.3 | 2.6 | 2.7 | 2.8 | 2.95 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.9 | 4.2 | 4.5 | 4.8 | 5.2 | 5.6 | 6.2 | 6.9 | 8 | 9.6 | 11.3 | 11.9 | 14.4 | 18.5 | 23.7 | 30.7 | 38.8 | 45.1 | 59.9 | 73.2 | 88.2 | 101.6 | 116.2 | 169.5 | 240.9 | 267.4 | 289.6 | 322.4 | 377
ASCO 15 | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 5 | 12 | 1100
ASCO 20 | 1.4 | 1.4 | 1.5 | 1.5 | 1.6 | 1.7 | 1.9 | 2.6 | 3.5 | 5.1 | 176.5 | 288
ResolutionAir Pinch | 1 | 1 | 1 | 1.1 | 1.3 | 1.5 | 2.6 | 4.3 | 9.2 | 18.9 | 57.2
Bronkhorst F004 | 35.4 | 35.5 | 36.1 | 37.1 | 38.4 | 39.6 | 44.2 | 66.1 | 69 | 124.3 | 1550 | 1900 | 3000
Notes: Aggiungi valvole mancanti

## Slide 8: Installed valves
Chart: Burkert 9.5 - R134a
| 100 | 90 | 80 | 70 | 60 | 55 | 50 | 45 | 40 | 30 | 20
Burkert 285 l/h | 1 | 1 | 1 | 2 | 2 | 3 | 8 | 30 | 104 | 266 | 447
manual 285 l/h | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 5 | 9 | 27 | 290
Chart: Burkert 8 - R134a
| 100 | 70 | 50 | 40 | 35 | 30 | 25 | 20 | 15
Burkert 285 l/h | 1 | 2 | 7 | 75 | 179 | 284 | 414 | 518 | 633
manual 285 l/h | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 5 | 9 | 27 | 290
Chart: ASCO 15 - R134a
| 100 | 90 | 80 | 70 | 60 | 55 | 50 | 45 | 40 | 35 | 30 | 25 | 20 | 17.5
ASCO 15 285 l/h | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 4 | 10 | 481
manual 285 l/h | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 5 | 9 | 27 | 290
Chart: GULEX MOTOR – N2
| 100 | 90 | 80 | 70 | 65 | 60 | 55 | 50 | 45 | 40 | 35 | 30 | 25 | 20 | 15 | 10 | 5 | 3 | 0
GULEX 16 l/min | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 5 | 7 | 10 | 30 | 68 | 443
manual 16l/min | 1.9 | 2 | 2 | 2 | 2.1 | 2.3 | 3 | 3.5 | 4.6 | 5.7 | 9.5 | 76.2 | 398.8

## Slide 9
Comparison Burkert VS Manual
Chart: N2 flow 16l/min
| 100 | 90 | 80 | 75 | 70 | 69 | 68 | 67 | 66 | 65 | 64 | 63 | 62 | 61 | 60 | 59 | 58 | 57 | 56 | 55 | 54 | 53 | 52 | 51 | 50 | 49 | 48 | 47 | 46 | 45 | 44 | 43 | 42 | 41 | 40 | 39 | 35 | 30 | 25 | 20 | 10 | 0
Burkert 8 mm | 2.1 | 2.2 | 2.8 | 3.2 | 3.6 | 3.7 | 3.8 | 3.9 | 4.1 | 4.2 | 4.4 | 4.5 | 4.7 | 5 | 5.3 | 5.6 | 6 | 6.3 | 6.6 | 7 | 7.7 | 8.4 | 9.7 | 11 | 11.5 | 13.2 | 15.4 | 19.3 | 21.5 | 25.4 | 28.8 | 35.4 | 42.6 | 51.8 | 66.7 | 80.7 | 140.8 | 200.5 | 227.8 | 270.4 | 320 | 377
Burkert 9.5 mm | 1.9 | 2 | 2.2 | 2.3 | 2.6 | 2.7 | 2.8 | 2.95 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.9 | 4.2 | 4.5 | 4.8 | 5.2 | 5.6 | 6.2 | 6.9 | 8 | 9.6 | 11.3 | 11.9 | 14.4 | 18.5 | 23.7 | 30.7 | 38.8 | 45.1 | 59.9 | 73.2 | 88.2 | 101.6 | 116.2 | 169.5 | 240.9 | 267.4 | 289.6 | 322.4 | 377
Manual | 1.9 | 2 | 2 | 2 | 2.1 | 2.3 | 3 | 3.5 | 4.6 | 5.7 | 9.5 | 76.2 | 398.8
Chart: N2 flow 16l/min
| 100 | 90 | 80 | 75 | 70 | 69 | 68 | 67 | 66 | 65 | 64 | 63 | 62 | 61 | 60 | 59 | 58 | 57 | 56 | 55 | 54 | 53 | 52 | 51 | 50 | 49 | 48 | 47 | 46 | 45 | 44 | 43 | 42 | 41 | 40 | 39 | 35 | 30 | 25 | 20 | 10 | 0
Burkert 8 mm | 2.1 | 2.2 | 2.8 | 3.2 | 3.6 | 3.7 | 3.8 | 3.9 | 4.1 | 4.2 | 4.4 | 4.5 | 4.7 | 5 | 5.3 | 5.6 | 6 | 6.3 | 6.6 | 7 | 7.7 | 8.4 | 9.7 | 11 | 11.5 | 13.2 | 15.4 | 19.3 | 21.5 | 25.4 | 28.8 | 35.4 | 42.6 | 51.8 | 66.7 | 80.7 | 140.8 | 200.5 | 227.8 | 270.4 | 320 | 377
Burkert 9.5 mm | 1.9 | 2 | 2.2 | 2.3 | 2.6 | 2.7 | 2.8 | 2.95 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.9 | 4.2 | 4.5 | 4.8 | 5.2 | 5.6 | 6.2 | 6.9 | 8 | 9.6 | 11.3 | 11.9 | 14.4 | 18.5 | 23.7 | 30.7 | 38.8 | 45.1 | 59.9 | 73.2 | 88.2 | 101.6 | 116.2 | 169.5 | 240.9 | 267.4 | 289.6 | 322.4 | 377
Manual | 1.9 | 2 | 2 | 2 | 2.1 | 2.3 | 3 | 3.5 | 4.6 | 5.7 | 9.5 | 76.2 | 398.8

## Slide 10: What’s installed in USC
Burkert 8mm
Burkert 9.5mm
ASCO DN20
ROTAREX MANUAL VALVE WITH GULEX ELECTRIC MOTOR
4
3
1
VALVE | WHERE | TYPE | FEEDBACK | COST [CHF]
BURKERT 8mm | BARREL 74 (RB-2 top) | SOLENOID | no | 420
BURKERT 9.5mm | BARREL 69 (RB-2 bottom) |  |  | 
 |  |  |  | 340
ROTAREX WITH GULEX MOTOR | BARREL 70 (RB-1 bottom) | ACTUATED | yes | 1400
ASCO DN20 | ENDCAP 83 | SOLENOID | yes | 315
2

## Slide 11: Installation in USC
1&2
3
4
Rack 83
Rack 69 & 74
Rack 70

## Slide 12: First tests on the real systems
Chart: Barrel 70 (RB-1 bottom) - GULEX
Chart: %opening
 | [mbar]
100-70 | 0
70-60 | 0.05
60-50 | 0.05
50-45 | 0.05
45-40 | 0.05
40-35 | 0.05
35-30 | 0.06
30-25 | 0.06
25-20 | 0.06
20-15 | 0.15
100-70 | 0
70-60 | 0.05
60-50 | 0.05
50-45 | 0.05
45-40 | 0.05
40-35 | 0.05
35-30 | 0.06
30-25 | 0.06
25-20 | 0.06
20-15 | 0.15
Notes: Limited at 15%

## Slide 13: First tests on the real systems
Chart: Barrel 69 (RB-2 bottom) - Burkert 9.5
Chart: %opening
 | [mbar]
100-90 | 0
90-80 | 0.02
80-70 | 0.11
70-65 | 0.3
65-60 | 0.15
100-90 | 0
90-80 | 0.02
80-70 | 0.11
70-65 | 0.3
65-60 | 0.15
Notes: Limited at 50%

## Slide 14
Chart: Barrel 74 (RB-2 top) - Burkert 8mm
Chart: %opening
First tests on the real systems
 | [mbar]
100-90 | 0
90-80 | 0.15
80-70 | 0.25
70-65 | -
100-90 | 0
90-80 | 0.15
80-70 | 0.25
70-65 | -
Notes: Limited at 53%

## Slide 15: Next steps
Other valves still under discussion/test
1. Resolution air pinch valve
Von Rohr
Econex
1
2
3
Other tests in USC
Auto regulation on dummy chambers
Different pressure and flow conditions
Regulation with manual valves completely open