Present (21): Markus Zerlauth (Chair), Andrzej Siemko, Arjan Verweij, Jan Uythoven, Felix Rodriguez Mateos, Reiner Denz, Mirko Pojer, Alain Antoine, Jens Steckert, Bozhidar Panev, Daniel Calcoen, Gert-Jan Coelingh, David Carrillo, Mateusz Jakub Bednarek, Giorgio D’Angelo, Edward Nowak, Jean-Christophe Garnier, Richard Mompo, Stephen Pemberton, Vincent Froidbise, Zinour Charifoulline (scientific secretary)

## Approval of the minutes of the meeting

NA as first meeting.

## LS2 IST Coordination - Introduction and proposed strategy

Markus presents slides with introduction, mandate, proposed attendance, as well as a proposal to discuss and agree on the groups organisation strategy for IST tests of MPE deliverables (#slides).

The proposed roadmap and organisation is as follows:

- Proposed organisation

  - Phase 1

    - Review and update IST procedures for each (sub)system

    - Add/update dependencies on infrastructure for tests, (SW) tools and provide resources estimates

  - Phase 2

    - Establish resources loaded planning for all activities and cross-check integration in global planning for those required

  - Phase 3

    - Common/centralised tracking during execution

- Propose to organise regular meetings, every two weeks

  - Initial focus on first round of discussion for updated IST documents of each system

  - Feedback to planning team to finalise by mid-June updated Master planning reflecting MPE needs

- Time-slot for meetings to be identified, propose to alternate with SB or MPE-TM slot

- Meeting invitation to be distributed to entire mailing list (but up to judgment of people if their attendance is required as a function of topic discussed)

Attendance/membership (MPE-IST-coordination-LS2@cern.ch)

MI: 		A. Antoine (PIC), R. Mompo (WIC), J. Uythoven

MS: 	J.C. Garnier (AccTesting), Z. Charifoulline + M. Zerlauth (IST coordination)

PE: 		A. Verweij (MP3)

EE: 		M. Bednarek + G. D’Angelo (ELQA, CL Heating System)

E. Nowak + D. Carrillo (DQHDS)

M. Pojer (SCT), F. Rodriguez Mateos

G.J. Coelingh + S Pemberton (600A EE), B. Panev (13kA EE, Conical Joints)

EP: 		D. Calcoen (DYPQ), J. Steckert + R. Denz + V. Froidbise (QDS/QPS, Conical Joints)

MPE: 	A. Siemko

Questions and discussions:

- Jan expressed his agreement with the items “Out of scope” of the IST coordination initiative; Andrzej agreed as well, emphasizing that one of the main objectives is to establish a resource loaded planning including all activities of the group in the LHC

- Reiner commented that no dedicated procedure would be required for the ‘DYPQ’, instead it will be part of standard QPS IST procedures through a dedicated update of the chapter for the main quadrupole tests. The document is already under revision and could be presented din one of the future meetings.

- Andrzej asked whether a heater firing campaign has to be re-done after the reinstallation and re-cabling of the DYPQ cabling. Reiner confirmed that this will be done as part of HWC. Markus commented that a small detailed procedure (including the needs for special software) should be either included in the QPS IST or established in a dedicated document.

- Arjan reminds that in the past, early phases of HWC often included considerable debugging and commissioning of software tools and proposed to profit from the IST phase to validate as well SW tools as much as possible. Markus agreed that this is an important step and proposed to get some feedback about the most recurrent SW issues MP3 encountered during early HWC to try addressing them early in IST tests or the testbed in b272.

- Reiner comments that NXCALS is still not in good shape. Markus agreed that it is not yet operation ready, however the imminent re-start of the injector complex will assure its readiness as well for IST in the LHC.

- Felix agreed that we also have to establish a dedicated procedure for the upgraded CL Heating System and proposed that Giorgio is the main contact person for it.

- Arjan asks about any changes in IST tests for dipole circuits with 11T. Jens and Reiner confirmed that this is indeed a major singularity for iQDS and nQPS. A special chapter is foreseen in the IST procedure dedicated to this topic (nQPS cabling check and new reference magnets, trim circuit, etc).

- After the meeting, Edward suggested to include for information (and eventual attendance) the mpe-standby-service in the distribution list for these meetings.

Actions:

- Include mpe-standby-service list in CC for future meeting invitations – Markus, Zinur

- Identify recurrent SW issues during early HWC and organise dry-run – Arjan, Markus, Zinur

## Updated IST procedure for 13kA EE systems

Bozhidar presented the updated IST procedure for the 13kA EE system (#slides, #procedure).
During the presentation, an emphasis was given to the main changes, an estimation of manpower needs / phase, and the dependencies of tests on general services and other infrastructure. The procedure document itself had been already distributed few weeks before in EDMS, final comments are being collected with the document currently in the approval stage.

Questions and discussions:

- On slide 6, Zinur asks about controls system and software tools to be used during the three different test categories. Bozhidar replies that no dedicated SW tools are required, test are using QPS Expert tools while measurements are done with dedicated instruments and results recorded manually. He noted that the availability of the PM browser is important for the validation of tests with current.

- Reiner, Jens and Mirko commented about the two uQDS portable chassis which are planned to be uses for resistance measurements (conical joints) in every point in the tunnel. Due to the limited availability of uQDS systems we will have to move them between the different SCT tests, it is however important that they are ready in time along with their dedicated firmware. Bozhidar confirmed that the readout SW (initially prepared by Szymon) is ready.

- Zinur asks about the IST test reports – when and where they will be stored? Bozhidar answers that the documents will be created at the end of each system tests and will be stored in EDMS. Andrzej comments that this should be done on a “sector by sector” basis.

- Edward comments that the logging and PM data acquisition were acquired during previous test campaigns with current and proofed to be useful to interpret and to understand the test on the fly.

- Mirko comments that a precise and well-prepared sequences of the 13kA EE system IST will be very important (since it requires the availability of many other systems like PC, WiFi, water cooling, SC tests, control system, …). The activity should be well coordinated with Marzia.

Actions:

- Follow-up readiness of uQDS crates for SCT campaign – Mirko, Reiner

- Follow-up availability and readiness of PM browser for SCT campaign – Markus, Zinur, JC

- Add to the IST procedure additional details about initial verification and related acceptance criteria for measurements of conical joints during IST phases - Bozhidar

Minutes prepared by Z. Charifoulline and M. Zerlauth