| Monday integration meeting Monday 27/04/2020 |  |  |  |  |
| --- | --- | --- | --- | --- |
| item | Sub-item | description | Action | Due date/status |
| 1 |  | Increase dimension of the US-UW at point 1. Agreed to go ahead after discussion with SMB project management on the 23/03/2020 Agreed that tolerance layer cannot be taken out |  |  |
|  | 1 | Halfen rail position to be changed | EL | Input provided |
|  | 2 | Meeting was held on Friday 27/03 . 1st phase are activities not pending from change of section of the PM List of changes agreed. Status on the 20/04/20 as provided by SMB: modified a part of internal structures, below the modifications done in the Catia hybrid model ST1305501_01 : • Partition wall between US & UW : moving of 500mm to UW side • UW17 : o decreasing of the width of the pit for false floor at ground level of 500mm o internal structures updated consequently to partition wall modification : steel structures moved by 500mm • Safe room : o moving by 200mm to vault direction (transversally), including pit and walls. o Keeping same layout for steel structure on top of the safe room, by increasing 200mm the cantilever of the roof concrete slab • Stairs for access to 1st level : moving by 200mm to UA17 direction + adaptation of steel structure • Steel platform for EN/EL below the vault (level +19.15) o Increasing dimension by 500mm to UW side o Increasing dimension by 200mm to UA17 side Some corrections & modifications of concrete invert are remaining, they will be done by our Consultants asap : • adaptations of openings of the sumps (see EN/CV email of previous week) • corrections of the technical duct position connected to UR15 • corrections of manholes positions Next meeting set for the week between the 11 and 15 may 2020 | INT, EL,CV, SMB |  |
|  | 3 | Confirmation of change/not change PM diameter | SMB | pending |
|  | 4 | Completion of redesign of all structure | ALL | 30/06/2020 |
| 2 |  | Models of the various UPR to be provided to prepare installation |  |  |
|  | 1 | UPR_UA57. | SMB | Done |
|  | 2 | UPR_UA17. New model with correction has been requested by SMB to the consultant. All models are needed to prepare the installation. New dates are proposed taking into account COVID impact. In parentheses old ones | SMB | 27/04/2020 (16/03/2020) |
|  | 3 | UPR_UA13. See above | SMB | 15/05/2020 (13/04/2020) |
|  | 4 | UPR_UA53. | SMB | 15/06/2020 (11/05/2025) |
|  | 5 | As we have received the UAs and ULs in P1 update the integration models with the new CE model (after green light from SMB) | INT | Pending |
| 3 |  | Review of the technical galleries P5 plus He tank slab |  |  |
|  | 1 | SH57 WP9 checking the seismological computations |  |  |
| 4 |  | Review of the technical galleries at P1 |  |  |
|  | 1 | Add reservation for the grounding sockets in the 3D P1 | SMB | 15/04/2020 |
|  | 2 | Check the connection for cameras and public lightening | SMB/EL | 14/04/2020 |
|  | 3 | Re-route cable trays in the trench from SD to SE1 and provide feed back to SMB. Modifications to be added to the SMR. Rerouting done. EL and SMB to perform final check and SMB modify slope at the entrance | EL | 14/04/2020 |
|  | 4 | Solution for accessing the technical gallery from the SU (proposed by SMB) accepted | SMB | DONE |
|  | 5 | SMB add to the model the start of the SE1 including the part to be modified | SMB | 14/04/2020 |
|  | 6 | SHE17 check ongoing. Specific meeting to be set for next week |  |  |
| 5 |  | Change of the UPS dimensions impacting the design of the racks support on the top of the safe room |  |  |
|  | 1 | US17: consultant acknowledged that they will integrate request. Agreed to have model when the change of the US dimensions will be also implemented |  | Summer 2020 |
|  | 2 | US57: EL check consultant proposal and spotted problems (see indico contribution). SMB to ask correction to the consultant | SMB | TBD |
| 6 | 1 | Position of the controls of the actuators of the smoke exhaust. Initial proposal for initial integration provided by INT and discussed. New iteration discussed and approved. To apply it also to building of point 5 Paolo to send mail to Timo. | INT | 27/04/2020 |
|  | 2 | More general discussion to be managed by Timo | 17.5 | pending |
| 7 |  | At point 1 the halfen scheme has been changed by the contractor in a not acceptable way |  |  |
|  | 1 | SMB circulated new proposals coming from Contractor. This is an extra not foreseen iteration. Checked with EL and counterproposal provided | SMB/EL | DONE |
|  | 2 | Confirm that it can be modified according to the EL requirement and modify the correlated models | SMB | 01/05/2020 |
| 8 |  | SMR SD17 and SD 57 completed | ALL | DONE |
| 9 |  | Organise revisions of SD doors P1 and P5 | SMB |  |
| 10 |  | Check if protection for the PM metallic structure have been added according to EROS request | SMB | 04/05/2020 |
| 11 |  | Agreed to start validation of the integration model that are synchro with the present SMRs being produced for the technical galleries and the He platforms. INT to drive the process | INT | 01/05/2020 |