## Slide 1: Measurements of the LHC (spare) UPS voltage spectra
G. Arduini, S. Kostoglou, Y. Papaphilippou, G. Sterbini
Measurements from EN-EL: J. Emonds-Alt, V. Chareyre,
P. Dominguez Chans, B. Saint Sulpice
Equipment: N. Biancacci, B. Salvant
Borri experts: F. Berti, F. Laponi
Valuable discussions & help: M. C. Bastos, M. Martino,
A. Lombardi, L. Timeo, D. Valuch
WP2, 15.09.2020
“Updates on noise studies” LMC 24/06/2020

## Slide 2: Motivation
To determine if the UPS is a potential candidate for the high-f cluster (7-8 kHz) observed on the LHC transverse beam spectrum:

## Slide 3: Motivation
To determine if the UPS is a potential candidate for the high-f cluster (7-8 kHz) observed on the LHC transverse beam spectrum:
  If UPS voltage spectrum contains 50 Hz harmonics.
“High-f cluster”
50 Hz harmonics
Transverse beam spectrum

## Slide 4: Motivation
To determine if the UPS is a potential candidate for the high-f cluster (7-8 kHz) observed on the LHC transverse beam spectrum:
  If UPS voltage spectrum contains 50 Hz harmonics.
  If spectral components are synchronized to the mains.
“High-f cluster”
“Low-f cluster”
Transverse beam spectrum

## Slide 5: Motivation
To determine if the UPS is a potential candidate for the high-f cluster (7-8 kHz) observed on the LHC transverse beam spectrum:
  If UPS voltage spectrum contains 50 Hz harmonics.
  If spectral components are synchronized to the mains.
First measurements of the LHC UPS voltage spectra complete. Based on the results & experience gained → propose tests with beam for Run 3.

## Slide 6: Outline
Introduction
Results: UPS voltage spectrograms
Conclusions & proposed tests for Run 3

## Slide 7: Outline
Introduction
Results: UPS voltage spectrograms
Conclusions & proposed tests for Run 3

## Slide 8: Introduction
ACin1
ACin2
* see appendix
Spare LHC UPS Borri B9000 100 kVA in BA7*.

## Slide 9: Introduction
ACin1
ACin2
* see appendix
Spare LHC UPS Borri B9000 100 kVA in BA7*.
Main UPS components: rectifier, battery & inverter. Expected UPS voltage spectrum: SF of inverter (and harmonics) & 50 Hz sidebands.

## Slide 10: Introduction
ACin1
ACin2
* see appendix
Spare LHC UPS Borri B9000 100 kVA in BA7*.
Main UPS components: rectifier, battery & inverter. Expected UPS voltage spectrum: SF of inverter (and harmonics) & 50 Hz sidebands.
Inverter’s switching frequency (SF) at 4 kHz.

## Slide 11: Introduction
Spare LHC UPS Borri B9000 100 kVA in BA7*.
Main UPS components: rectifier, battery & inverter. Expected UPS voltage spectrum: SF of inverter (and harmonics) & 50 Hz sidebands.
Inverter’s switching frequency (SF) at 4 kHz.
Important UPS operation modes*: normal mode, on battery, bypass
ACin1
ACin2
* see appendix

## Slide 12: Outline
Introduction
Results: UPS voltage spectrograms
Conclusions & proposed tests for Run 3

## Slide 13: Results: UPS spectra
Inverter’s SF & harmonics

## Slide 14: Results: UPS spectra
Inverter’s SF is clearly at 4 kHz.
Prior to LS1, the SF was at 8 kHz.
New UPS system was installed with SF at ~6.74 kHz* (not consistent with our observations).
Present measurements
Past measurements*
* V. Chareyre. Assessment of the High Frequency Noise Produced by the UPS Systems in the LHC Machine.

## Slide 15: Results: UPS spectra
Inverter’s SF is clearly at 4 kHz.
Prior to LS1, the SF was at 8 kHz.
New UPS system was installed with SF at ~6.74 kHz* (not consistent with our observations).
→ The revolution and betatron frequency should always be considered when selecting SF.
Present measurements
Past measurements*
* V. Chareyre. Assessment of the High Frequency Noise Produced by the UPS Systems in the LHC Machine.

## Slide 16: Results: UPS spectra
Spectral components around SF and its harmonics are 50 Hz harmonics.

## Slide 17: Results: UPS spectra
Spectral components around SF and its harmonics are 50 Hz harmonics.
50 Hz sidebands are an expected feature as inverter relies on pulse-width modulation.
Slightly changing SF→ 50 Hz sidebands’ position would also change.

## Slide 18: Results: UPS spectra
Normal mode
Static bypass
Noise from the mains
Noise from the inverter
Switching UPS mode from normal to static bypass → UPS voltage spectrum changes.

## Slide 19: Results: UPS spectra
Normal mode
Static bypass
Noise from the mains
Noise from the inverter
Switching UPS mode from normal to static bypass → UPS voltage spectrum changes.
If source of high-f cluster is UPS, this modification should be detected on the beam’s spectrum.

## Slide 20: Results: UPS spectrograms
Normal mode
Without synchronization with ACin1 & 2
On battery
Clear synchronization with mains in normal mode.
Jittering not present when switching to battery mode and inhibiting synchronization.

## Slide 21: Outline
Introduction
Results: UPS voltage spectrograms
Conclusions & proposed tests for Run 3

## Slide 22: Conclusions
Goal of the study:
  To determine if UPS noise spectrum contains 50 Hz harmonics as observed on the LHC beam spectrum. Yes, 50 Hz harmonics around 4 kHz & 8 kHz (very close to betatron tune and alias).
  To determine if spectral components are synchronized to the mains as observed on the LHC beam spectrum. Yes, clear synchronization with mains in normal mode.

## Slide 23: Conclusions
Goal of the study:
  To determine if UPS noise spectrum contains 50 Hz harmonics as observed on the LHC beam spectrum. Yes, 50 Hz harmonics around 4 kHz & 8 kHz (very close to betatron tune and alias).
  To determine if spectral components are synchronized to the mains as observed on the LHC beam spectrum. Yes, clear synchronization with mains in normal mode.
Based on this signature, the UPS is a potential candidate for the high-f cluster.

## Slide 24: Conclusions
Goal of the study:
  To determine if UPS noise spectrum contains 50 Hz harmonics as observed on the LHC beam spectrum. Yes, 50 Hz harmonics around 4 kHz & 8 kHz (very close to betatron tune and alias).
  To determine if spectral components are synchronized to the mains as observed on the LHC beam spectrum. Yes, clear synchronization with mains in normal mode.
Based on this signature, the UPS is a potential candidate for the high-f cluster.
Tests with beam and different UPS configurations are needed to identify a correlation with the harmonics on the beam.

## Slide 25: Proposed tests with beam for Run 3
Perturb UPS noise spectrum and observe if reproducible effect on transverse beam spectrum.

## Slide 26: Proposed tests with beam for Run 3
Perturb UPS noise spectrum and observe if reproducible effect on transverse beam spectrum.
  Switch UPSs connected to ADT (2 in UX45 and 1 in SR4) from normal mode to static bypass with low intensity beam at injection.
  Similar test performed in the past without beam*. Important impact mainly from SR4.
  Remote operation not possible at the moment, new firmware required.
* see appendix

## Slide 27: Proposed tests with beam for Run 3
Perturb UPS noise spectrum and observe if reproducible effect on transverse beam spectrum.
  Switch UPSs connected to ADT (2 in UX45 and 1 in SR4) from normal mode to static bypass with low intensity beam at injection.
  Similar test performed in the past without beam*. Important impact mainly from SR4.
  Remote operation not possible at the moment, new firmware required.
* see appendix
SM18 warm measurements of LHC dipole transfer function up to 10 kHz.
Next steps

## Slide 28: Thank you for you attention

## Slide 29: Backup

## Slide 30: Measurement setup
UPS
Oscilloscope
4P breaker
Measurements in spare LHC UPS Borri B9000 100 kVA in BA7. Inverter’s SF at 4 kHz.
Sampling rate of 200 kHz, 10 s/acquisition & signals of 3 phases.

## Slide 31: UPS operation modes
ACin1
ACin2
Normal mode: ACin1 → Rectifier→ Inverter→ Load
Synchronized to bypass (ACin2) through internal inverter PLL.

## Slide 32: UPS operation modes
ACin1
ACin2
Normal mode: ACin1 → Rectifier→ Inverter→ Load
Synchronized to bypass (ACin2) through internal inverter PLL.
On battery: Battery→ Inverter→ Load
In case of power failure.

## Slide 33: UPS operation modes
ACin1
ACin2
Normal mode: ACin1 → Rectifier→ Inverter→ Load
Synchronized to bypass (ACin2) through internal inverter PLL.
On battery: Battery→ Inverter→ Load
In case of power failure.
Static bypass: ACin2 → Switch → Load
Switches automatically to maintain power continuity in case of inverter failure.

## Slide 34: Past measurements with UX45 & SR4 UPSs to bypass
D. Valuch