## Slide 1: Heat loads and cryogenics
L.Tavian, D. Delikaris
CERN, Cryogenics Group, Technology Department
Accelerators & Technology Sector

## Slide 2: Content
Introduction
Heat loads
  Heat inleaks
  Resistive heating
  Beam induced heat load
Cooling capacity requirement
Conclusions

## Slide 3
Chart: Helium refrigeration capacity at CERN (kW@4.5 K)
| 1960 | 1962 | 1963 | 1967 | 1968 | 1971 | 1973 | 1975 | 1978 | 1991 | 1992 | 1993 | 1994 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
 | 0 | 0 | 0.5 | 0.5 | 1 | 1 | 3 | 3 | 7 | 7 | 19 | 43 | 67 | 67 | 90 | 90 | 90 | 126 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
Cryogenics at CERN
HE-LHC

## Slide 4: Introduction
Scaling from LHC loads
Three main temperature levels
  Thermal shield (TS): 50 and 75 K
  Heat intercept (HI): 4.6 K & Beam screen (BS): 4.6-20 K (40-60 K or 85-100 K as an alternative compatible with vacuum specification)
  Cold mass(CM): 2 K
8 cryogenic sectors
  One cryogenic plant per continuous cryostat (arc + dispersion suppressors)
  Dedicated cryogenic plants for high-load insertions (RF, IT…) as for HL-LHC
Continuous cryostat (arc + dispersion suppressors) only considered in the following

## Slide 5: Heat inleaks (w/o contingency)
Assumption: thermal performance of the HE-LHC cryostat (magnet + cryogenic distribution QRL) similar to the one of the LHC cryomagnet.
Temperature level |  | LHC | HE-LHC
TS (50-75 K) | [W/m] | 7.7 | 7.7
HI (4.6 K) | [W/m] | 0.23 | 0.23
CM (2 K) | [W/m] | 0.21 | 0.21
Contingency (on heat inleaks); Reminder: LHC contingency factor = 1.5
Overcapacity (on cryogenic plant’s refrigeration power)

## Slide 6: Resistive heating in SC splices
Resistive heating proportional to:
  the square of the magnet current,
  the splice electrical resistance
  the number of splices
 |  | LHC nominal | HE-LHC
Main magnet current | [kA] | 12 | 18
Splice resistance | [nOhm] | 0.5 | 0.5
Number of splice per arc | [-] | 2500 | 3750
Resistive heating on CM | [W/m] | 0.1 | 0.34

## Slide 7: Current lead cooling
Assumptions:
  HE-LHC is using the same type of HTS current lead as the LHC with the same cooling performance, i.e. 54 mg/s per kA of helium between 20 and 300 K
  as the optics of the HE-LHC are not yet fully defined the number of individually powered magnets is not known  total current entering or exiting proportional to the main magnet current
  as for the LHC, it is assumed that high-load sectors enter two times more current than low-load sectors
 |  | LHC nominal | HE-LHC
Main magnet current | [kA] | 12 | 18
Total current in/out | [kA] | 2750 | 4130
Total current high load sector CC | [kA] | 460 | 690
Total current low load sector CC | [kA] | 230 | 345
Specific CL cooling flow | [mg/s per kA] | 54 | 54
High-load sector CL cooling flow | [g/s] | 25 | 37
Low-load sector CL cooling flow | [g/s] | 12 | 19

## Slide 8: Beam-induced load: Scaling laws
Beam-induced load | Energy E | Bunch Population Nbunch | Bunch Number nbunch | Bunch Length σz [rms] | Beam-screen aperture b | Temp. Level
Synchrotron radiation | E4 | Nbunch | nbunch |  |  | BS
Image current |  | Nbunch2 | nbunch | σz-3/2 | b-1 | BS
Photo-electron cloud |  | Nbunch3 | nbunch |  | b-2 | BS
Beam gas scattering |  | Nbunch | nbunch |  |  | CM

## Slide 9: Beam-induced loads (for BS operating between 4.6 and 20 K)
The biggest change concerns the synchrotron-radiation load, which increases by a factor 17 !
 |  | LHC nominal | HE-LHC
Beam energy, E | [TeV] | 7 | 16.5
Bunch population, Nbunch | [1011 p] | 1.15 | 1.29
Bunch number, nbunch | [-] | 2808 | 1404
Bunch length, σz [rms] | [cm] | 7.55 | 6.55
Beam-screen aperture radius, b | [cm] | 2 | 1.3
Synchrotron radiation | [W/m] | 0.33 | 5.71
Image current | [W/m] | 0.36 | 0.44
Photo-electron cloud | [W/m] | 0.90 | 1.50
Beam gas scattering | [W/m] | 0.05 | 0.03

## Slide 10: Operating the beam screen at higher temperature
Operating beam screen at higher temperature will reduce the specific entropic cost of refrigeration, but:
  As the electrical resistivity of the copper on the beam-screen surface increases with the temperature, the image-current load will also increase proportionally
  The temperature difference between the beam screen and the cold bore will increase, i.e. the heat inleaks on the cold mass will increase as well
  Changing the operating conditions and the specific heat load has a direct impact on the cooling capillary diameter
Two alternative temperature ranges compatible with vacuum requirement:
  40-60 K
  85-100 K

## Slide 11: Copper electrical resistivity
Image current: 0.44 W/m for 4.6-20 K temperature range 2.4 W/m for 40-60 K temperature range 9.8 W/m for 85-100 K temperature range
X 5.5
X 22

## Slide 12: CM heat load vs. BS temperature
Cold bore heat load: 0.006 W/m for 4.6-20 K temperature range 0.17 W/m for 40-60 K temperature range 0.71 W/m for 85-100 K temperature range
X 30
X 120
(See LHC Project Note 330)

## Slide 13: Beam screen cooling capillary
40-60 K temperature range  minimum diameter !
 | LHC | HE-LHC |  | 
BS@ | 4.6-20 K | 4.6-20 K | 40-60 K | 85-100 K
Inlet temperature [K] | 4.6 | 4.6 | 40 | 85
Inlet pressure [bar] | 3.0 | 3.0 | 20 | 20
Outlet temperature [K] | 20 | 20 | 60 | 100
Outlet pressure [bar] | 1.3 | 1.3 | 18 | 18
Specific heat load [W/m] | 4.8 | 7.65 | 9.45 | 16.3
Loop length [m] | 50 | 50 | 50 | 50
Number of capillary per aperture | 2 | 2 | 2 | 2
Capillary inner diameter [mm] | 3.7 | 4.4 | 3.8 | 6.0

## Slide 14: Summary of specific cryogenic heat loads
Temp. level | Heat load source |  | LHC nominal | HE-LHC |  | 
 |  |  |  | BS @ 4.6-20 K | BS @ 40-60 K | BS @ 85-100 K
TS | Heat inleaks Total TS | [W/m] [W/m] | 7.7 7.7 | 7.7 7.7 |  | 
HI | Heat inleaks Total HI | [W/m] [W/m] | 0.23 0.23 | 0.23 0.23 |  | 
BS | Heat inleaks Synchrotron radiation Image current Photo-electron cloud Total BS | [W/m] [W/m] [W/m] [W/m] [W/m] | 0 0.33 0.36 0.90 1.82 | 0 5.71 0.44 1.50 7.65 | -0.17 5.71 2.40 1.50 9.45 | -0.71 5.71 9.81 1.50 16.3
CM | Heat inleaks Resistive heating Beam-gas scattering Total CM | [W/m] [W/m] [W/m] [W/m] | 0.21 0.10 0.05 0.36 | 0.21 0.34 0.03 0.58 | 0.38 0.34 0.03 0.74 | 0.92 0.34 0.03 1.29

## Slide 15: Cold mass cooling
LHC cooling scheme limited to 0.9 W/m (sub-cooling heat exchanger), i.e. not compatible with the 85-100 K BS temperature range.
Cooling at 2 K: reduced conduction in superfluid helium to extract the heat from the coil.
Apparent
thermal conductivity of superfluid helium
LHC
HE-LHC

## Slide 16: Continuous cryostat cooling capacity per sector (values in brackets: equivalent entropic capacity in kW at 4.5 K)
Temperature level | HE-LHC continuous cryostat |  |  | LHC high-load sector
 | BS @ 4.6-20 K | BS @ 40-60 K | BS @ 85-100 K | BS @ 4.6-20 K
TS (50-75 K) [kW] | 32 (2.2) |  |  | 33 (2.2)
HI (4.6-20 K) [kW] | 33 (18.4) | 1.0 (0.5) | 1.0 (0.5) | 7.7 (4.3)
BS [kW] |  | 40 (3.5) | 69 (3.3) | 
CM (2 K) [kW] | 2.4 (7.8) | 3.1 (10.0) | 5.4 (17.4) | 2.7* (9.3)
CL [g/s] | 56 (2.5) |  |  | 41 (1.8)
Total equivalent entropic capacity | (30.8) | (18.6) | (25.8) | (17.6)
*: 2.4 kW at 1.8 K plus 0.3 kW at 4.5 K
Assumptions: - Continuous cryostat length: 2800 m - Overcapacity factor: 1.5 (for each temperature level) as for LHC plants

## Slide 17: Equivalent entropic capacity

## Slide 18: Electrical input power for continuous-cryostat refrigerators
 |  | HE-LHC CC refrigerator |  |  | LHC refrigerator
 |  | BS @ 4.6-20 K | BS @ 40-60 K | BS @ 85-100 K | 
Electrical input power per refrigerator | [MW] | 7.7 | 4.7 | 6.5 | 4.4
Number of refrigerator | [-] | 8 | 8 | 8 | 8
Total electrical input power | [MW] | 62 | 37 | 52 | 35
Assuming a performance coefficient factor of 250 W/W (electrical / @4.5 K)

## Slide 19: Concluding remarks [1/2]
No contingency has been introduced in the numbers
A lot of assumptions have to be confirmed ( e.g. the splice resistance and number, the main magnet current, the current-leads distribution and number, and the cryostat performance)
The optimization of the refrigeration cycle has still to be done (wrt temperature levels)
Transient heat loads (ramp/de-ramp, fast de-ramp, quench), have still to be considered in order to define the correct level of buffering
The insertion loads have still to be considered (dedicated new cryoplants as for HL-LHC)

## Slide 20: Concluding remarks [2/2]
Depending on the cooling scenario, up to 9 temperature levels have to be distributed along the continuous cryostats to supply or recover the different cooling loops  A rationalization study has to be done for reducing the number of distribution headers like:
  operating the beam screen and the thermal shield with the same temperature range (40-60 K)
  cooling the resistive part of HTS current lead with a helium flow at a higher temperature and pressure (e.g. 40 K, 20 bar)
At the end of the LHC (2030), the LHC (& former LEP) cryogenics will reach 30 to 40 years operation; Initially specified for a 20-year operation, major overhauling has to be considered for the equipments re-affected to the HE-LHC project (cryoplants, QRL, distribution boxes…)

## Slide 21
Additional slide
Rationalization options
Temperature range (9 levels)
Inlet: 50 K (TS), 40 K (BS), 20 K (CL), 4.6 K
Outlet: 300 K (CL), 75 K (TS), 60 K (BS), 4 K (Very Low Pumping)
Quench recovery T
Rationalization options:
TS & BS @ 40-60 K
CL LHC 20-300 K (but regulated @ 50 K, saving distribution headers)
CL HE-LHC @ 40-300 K, 20b (taking profit from the TS & BS option)
Leading to reduced Temperature range (6 levels)
Inlet: 40 K, 20 b (TS, BS, CL), 4.6 K
Outlet: 300 K (CL), 60 K (TS, BS), 4 K (Very Low Pumping)
Quench recovery T